## Sheet1
Main steam flow (t/h) | Main steam temperature (boiler side) (℃) | Main steam pressure (boiler side) (Mpa) | Reheat steam temperature (boiler side) (℃) | Superheater desuperheating water flow (t/h) | Reheater desuperheating water flow (t/h) | Feedwater temperature (℃) | Feedwater flow (t/h) | Flue gas temperature (℃) | Boiler oxygen level (%) | Main steam temperature (turbine side) (℃) | Main steam pressure (turbine side) (MPa) | Reheat steam temperature (turbine side) (℃) | Reheat steam pressure (turbine side) (MPa) | Control stage pressure (Mpa) | High exhaust pressure (Mpa) | Feedwater pressure (MPa) | Condenser vacuum (kPa) | Circulating water outlet temperature (℃) | Cold Reheat Pressure (Mpa) | Cold Reheat Temperature (°C) | O2 in APH (%) | O2 Out APH (%) | Refference Temperature (°C) | Flue Gas in Temperature (°C) | Coal Flow (t/h) | NPHR (Kcal/Kwh) | Gross Load (MW) | Nett Load (MW) | HHV (Kcal/Kg) | Pressure HRH | Temperature HRH | Spray reheat pressure | Spray reheat temperature | Boiler Eff (%)
983.3645 | 568.099 | 15.9705 | 566.7198 | 128.1356 | 0.93515 | 258.0215 | 1035.7529 | 130.7081 | 3.8285 | 564.6478 | 15.8531 | 566.7198 | 2.244 | 12.2233 | 2.4973 | 17.4638 | -93.2548 | 36.5821 | 2.48 | 322.19 | 3.84 | 4.57 | 35 | 350.96 | 192.41 | 2607.2701 | 344.56 | 323.93 | 4389.4444 | 2.29 | 566.36 | 5.5 | 159.91 | 77.9157
903.3128 | 568.0238 | 14.9078 | 563.9857 | 119.6284 | 1.9447 | 253.7339 | 964.8674 | 129.804 | 3.6597 | 564.467 | 14.7994 | 563.9857 | 2.0627 | 11.3017 | 2.3003 | 16.311 | -93.3194 | 36.5445 | 2.28 | 320.5 | 3.77 | 4.36 | 33 | 350.79 | 181.37 | 2687.1217 | 316.02 | 296.27 | 4389.4444 | 2.1 | 565 | 5.11 | 149.95 | 76.2949
903.7344 | 568.6503 | 14.8692 | 565.6709 | 110.7852 | 1.4374 | 253.6135 | 959.4864 | 127.8601 | 3.5618 | 565.0773 | 14.7695 | 565.6709 | 2.0636 | 11.2692 | 2.3011 | 16.2636 | -93.3135 | 36.5518 | 2.28 | 320.8 | 3.84 | 4.41 | 33 | 350.13 | 178.47 | 2663.0321 | 314.22 | 294.17 | 4389.4444 | 2.09 | 565.63 | 5.08 | 149.38 | 77.8862
877.7676 | 568.2628 | 14.4228 | 564.2372 | 97.3075 | 0.98342 | 252.2173 | 938.4276 | 129.8129 | 3.9052 | 564.8285 | 14.3218 | 564.2372 | 2.0044 | 10.9876 | 2.2374 | 15.844 | -93.3464 | 36.5041 | 2.21 | 321.34 | 4.07 | 4.66 | 33 | 349.91 | 172.09 | 2651.9432 | 304.68 | 284.84 | 4389.4444 | 2.03 | 564.09 | 4.92 | 141.1 | 78.3676
921.2388 | 568.1025 | 15.2047 | 565.4749 | 93.6657 | 0.79809 | 254.272 | 974.6316 | 130.2184 | 3.8798 | 564.9458 | 15.0998 | 565.4749 | 2.1037 | 11.4759 | 2.3448 | 16.7141 | -93.2451 | 36.7042 | 2.32 | 320.44 | 3.85 | 4.4 | 34 | 354.42 | 181.74 | 2651.5244 | 320.94 | 300.86 | 4389.4444 | 2.13 | 565.75 | 5.23 | 148.33 | 77.8564
910.4299 | 568.2216 | 14.9737 | 566.7511 | 86.539 | 2.5897 | 253.6276 | 965.26 | 131.0958 | 4.0135 | 564.9905 | 14.8718 | 566.7511 | 2.0789 | 11.3497 | 2.3178 | 16.5137 | -93.2861 | 36.6219 | 2.3 | 320.36 | 3.98 | 4.47 | 34 | 354.56 | 180.86 | 2663.3842 | 317.95 | 298.07 | 4389.4444 | 2.11 | 566.91 | 5.17 | 150.77 | 77.5378
899.1002 | 568.6352 | 14.7529 | 566.5435 | 85.9652 | 2.5343 | 252.9364 | 951.0572 | 131.5366 | 3.9395 | 565.1651 | 14.6511 | 566.5435 | 2.0541 | 11.1969 | 2.2894 | 16.2428 | -93.3042 | 36.4831 | 2.26 | 321 | 4.22 | 4.72 | 33 | 357.11 | 176.59 | 2656.199 | 311.68 | 291.82 | 4389.4444 | 2.08 | 565.7 | 5.04 | 150.45 | 78.595
972.8159 | 568.1285 | 15.8888 | 565.0112 | 100.6617 | 4.0417 | 256.9598 | 1023.8225 | 132.2614 | 3.7805 | 564.8518 | 15.7803 | 565.0112 | 2.2196 | 12.0871 | 2.4718 | 17.4579 | -93.1676 | 36.5735 | 2.43 | 319.49 | 3.91 | 4.44 | 34 | 357.31 | 187.68 | 2604.1123 | 336.69 | 316.35 | 4389.4444 | 2.24 | 565.55 | 5.45 | 152.7 | 79.4347
986.0117 | 566.9578 | 15.9471 | 565.3325 | 118.1991 | 4.308 | 257.8493 | 1031.046 | 129.6246 | 3.9746 | 563.7457 | 15.8385 | 565.3325 | 2.2504 | 12.1974 | 2.5049 | 17.4903 | -93.0827 | 36.8061 | 2.48 | 319.62 | 3.88 | 4.56 | 33 | 357.14 | 186.41 | 2539.5293 | 343.27 | 322.2 | 4389.4444 | 2.29 | 566.37 | 5.52 | 157.45 | 81.1389
891.1803 | 567.8099 | 14.5524 | 566.1389 | 115.2644 | 1.8292 | 253.038 | 941.7067 | 128.3401 | 4.3076 | 564.2978 | 14.4553 | 566.1389 | 2.0371 | 11.0612 | 2.2709 | 15.9465 | -93.3236 | 36.278 | 2.25 | 322.44 | 4.16 | 4.78 | 35 | 351.65 | 170.17 | 2568.08 | 310.35 | 290.86 | 4389.4444 | 2.07 | 566.66 | 4.95 | 151.33 | 80.8521
863.7814 | 568.6101 | 14.1142 | 567.3463 | 125.4375 | 1.814 | 251.3425 | 920.6639 | 128.0674 | 4.1693 | 565.0496 | 14.0182 | 567.3463 | 1.9745 | 10.7608 | 2.2033 | 15.4323 | -93.5917 | 35.5297 | 2.19 | 322.5 | 3.87 | 4.45 | 34 | 345.63 | 166.85 | 2584.0759 | 302.67 | 283.42 | 4389.4444 | 2.01 | 567.13 | 4.81 | 150 | 79.9635
924.0751 | 568.5278 | 15.1108 | 567.4653 | 124.8868 | 3.825 | 254.4296 | 975.952 | 127.4952 | 3.8791 | 565.0711 | 15.0091 | 567.4653 | 2.1106 | 11.4817 | 2.3516 | 16.5004 | -93.3146 | 36.2354 | 2.34 | 320.65 | 3.64 | 4.2 | 34 | 348.94 | 179.71 | 2589.7146 | 323.86 | 304.6 | 4389.4444 | 2.15 | 567.61 | 5.21 | 153.51 | 79.2634
931.9485 | 568.2387 | 15.2417 | 566.7905 | 112.826 | 9.3178 | 254.7853 | 978.1932 | 130.7372 | 3.9034 | 564.8393 | 15.1409 | 566.7905 | 2.1291 | 11.5112 | 2.3714 | 16.6904 | -93.4432 | 35.8121 | 2.35 | 320.95 | 3.82 | 4.4 | 34 | 352.09 | 182.78 | 2631.7948 | 324.37 | 304.85 | 4389.4444 | 2.16 | 566.74 | 5.21 | 153.81 | 78.7679
944.3879 | 568.1876 | 15.5589 | 566.5336 | 101.1704 | 2.8148 | 256.0323 | 994.6506 | 130.3531 | 3.8013 | 564.6683 | 15.4551 | 566.5336 | 2.1562 | 11.7174 | 2.4017 | 17.0697 | -93.3444 | 36.1792 | 2.38 | 320.52 | 3.66 | 4.24 | 34 | 351.04 | 184.58 | 2614.4879 | 329.37 | 309.89 | 4389.4444 | 2.19 | 566.93 | 5.35 | 153.75 | 78.542
948.6966 | 568.8867 | 15.6226 | 566.7771 | 104.2771 | 2.2142 | 255.9136 | 1003.0553 | 131.9025 | 3.6294 | 565.3512 | 15.5206 | 566.7771 | 2.1657 | 11.8223 | 2.4129 | 17.1335 | -93.0918 | 36.8654 | 2.39 | 319.87 | 3.64 | 4.16 | 34 | 350.69 | 185.91 | 2620.1368 | 331.34 | 311.45 | 4389.4444 | 2.2 | 567.11 | 5.41 | 153.83 | 78.2945
900.4146 | 568.7918 | 14.9442 | 567.3723 | 114.1974 | 4.6827 | 252.9072 | 951.8942 | 128.4954 | 4.2674 | 565.3611 | 14.8528 | 567.3723 | 2.058 | 11.1765 | 2.2939 | 16.3437 | -93.3208 | 36.2094 | 2.27 | 320.9 | 4.46 | 4.98 | 33 | 348.15 | 174.61 | 2608.9829 | 313.07 | 293.77 | 4389.4444 | 2.09 | 567.53 | 5.09 | 152.65 | 79.6416
860.1206 | 568.3407 | 14.0996 | 566.088 | 104.5718 | 4.0277 | 250.943 | 916.1536 | 126.4889 | 4.7773 | 564.9601 | 14.0087 | 566.088 | 1.9662 | 10.7108 | 2.1942 | 15.5006 | -93.33 | 36.3184 | 2.17 | 322.57 | 4.96 | 5.48 | 35 | 348.72 | 169.14 | 2653.054 | 298.99 | 279.84 | 4389.4444 | 2 | 566.8 | 4.8 | 150.19 | 78.6139
887.7303 | 568.7855 | 14.6678 | 566.7252 | 97.7599 | 2.0811 | 252.3877 | 941.3993 | 128.2535 | 4.5723 | 565.3288 | 14.5755 | 566.7252 | 2.028 | 11.0678 | 2.2616 | 16.1255 | -93.3316 | 36.2715 | 2.25 | 321.5 | 4.84 | 5.35 | 34 | 353.91 | 176.81 | 2660.4198 | 310.7 | 291.72 | 4389.4444 | 2.07 | 567.09 | 5.03 | 151.46 | 77.5242
957.8843 | 568.0382 | 15.5527 | 566.0977 | 95.3482 | 2.2011 | 256.6644 | 1004.4152 | 133.0671 | 4.0434 | 564.3846 | 15.4405 | 566.0977 | 2.1866 | 11.8968 | 2.4352 | 17.1126 | -93.2298 | 36.4434 | 2.42 | 320.29 | 4.28 | 4.81 | 34 | 358.93 | 187.44 | 2609.195 | 335.11 | 315.33 | 4389.4444 | 2.23 | 566.33 | 5.39 | 154.81 | 78.4999
1078.9955 | 567.7571 | 16.6702 | 567.0384 | 119.0418 | 7.5031 | 262.5813 | 1122.9787 | 135.9829 | 3.3382 | 564.305 | 16.5297 | 567.0384 | 2.4594 | 13.4056 | 2.7333 | 18.3863 | -92.9616 | 36.9845 | 2.69 | 320.25 | 3.51 | 4.06 | 34 | 362.88 | 204.37 | 2537.1083 | 374.01 | 353.58 | 4389.4444 | 2.48 | 567.42 | 5.82 | 160.09 | 80.4799
1169.6887 | 567.9227 | 17.755 | 566.9739 | 147.1434 | 21.1153 | 267.0522 | 1201.1358 | 137.1192 | 3.6937 | 564.4688 | 17.6013 | 566.9739 | 2.6639 | 14.3957 | 2.957 | 19.5633 | -93.0942 | 36.3056 | 2.92 | 319.99 | 3.58 | 4.21 | 34 | 369.62 | 220.06 | 2496.9398 | 408.34 | 386.85 | 4389.4444 | 2.71 | 567.31 | 6.22 | 164.98 | 80.9534
1112.346 | 568.6369 | 17.1164 | 567.0643 | 104.9449 | 8.2466 | 264.6807 | 1155.3375 | 135.0923 | 3.7253 | 564.7176 | 16.9649 | 567.0643 | 2.5341 | 13.8157 | 2.8157 | 18.9545 | -92.7988 | 37.2173 | 2.79 | 319.82 | 3.81 | 4.47 | 34 | 363.93 | 215.77 | 2573.6696 | 389.2 | 368 | 4389.4444 | 2.58 | 567 | 6.07 | 162.28 | 78.3173
1092.0456 | 568.6244 | 17.1529 | 565.6656 | 81.3945 | 5.4241 | 263.6309 | 1139.2382 | 134.4151 | 3.4734 | 564.9538 | 17.0118 | 565.6656 | 2.4885 | 13.5876 | 2.7664 | 18.9846 | -92.789 | 37.2447 | 2.73 | 319.44 | 3.87 | 4.43 | 35 | 359.69 | 214.99 | 2620.1873 | 381.01 | 360.16 | 4389.4444 | 2.53 | 566.42 | 6.03 | 160.3 | 77.0597
1057.2972 | 568.4507 | 16.7288 | 567.0161 | 88.061 | 7.5727 | 261.0561 | 1098.1577 | 134.5346 | 3.7659 | 564.9234 | 16.596 | 567.0161 | 2.4103 | 13.0713 | 2.6792 | 18.4831 | -93.2038 | 36.1229 | 2.66 | 319.5 | 3.99 | 4.52 | 35 | 361.45 | 207.21 | 2597.7859 | 370.75 | 350.12 | 4389.4444 | 2.46 | 566.82 | 5.89 | 159.37 | 78.0713
944.5181 | 568.7631 | 15.4599 | 566.6741 | 93.6134 | 3.7579 | 255.4403 | 998.3379 | 131.1134 | 4.5912 | 565.3306 | 15.3519 | 566.6741 | 2.1555 | 11.7551 | 2.4007 | 17.0468 | -93.2588 | 36.2397 | 2.37 | 320.42 | 4.84 | 5.3 | 34 | 358.55 | 188.35 | 2675.2261 | 328.81 | 309.04 | 4389.4444 | 2.19 | 566.6 | 5.34 | 152.69 | 77.0264
1070.2511 | 568.5018 | 16.7053 | 567.1153 | 111.6145 | 5.2883 | 262.3654 | 1118.98 | 133.2852 | 3.8139 | 564.9118 | 16.5602 | 567.1153 | 2.4395 | 13.3216 | 2.7111 | 18.4434 | -93.0494 | 36.4977 | 2.66 | 319.99 | 4.17 | 4.73 | 35 | 361.55 | 210.7 | 2637.9234 | 371.12 | 350.6 | 4389.4444 | 2.46 | 566.86 | 5.84 | 159.05 | 77.2486
1076.9807 | 568.5788 | 16.7404 | 567.5423 | 110.8249 | 6.3319 | 262.7976 | 1120.9994 | 136.8253 | 3.5017 | 564.859 | 16.5991 | 567.5423 | 2.4542 | 13.3584 | 2.728 | 18.4893 | -93.0635 | 36.442 | 2.7 | 319.81 | 3.82 | 4.33 | 34 | 363.73 | 207.55 | 2565.4122 | 375.83 | 355.12 | 4389.4444 | 2.49 | 566.9 | 5.91 | 160.55 | 79.0312
1187.7108 | 568.6718 | 17.8824 | 567.5047 | 98.5686 | 10.2653 | 267.9723 | 1229.1057 | 138.3735 | 3.4346 | 564.731 | 17.7122 | 567.5047 | 2.702 | 14.7853 | 3.0007 | 19.8723 | -92.6771 | 37.2917 | 2.96 | 319.18 | 3.63 | 4.19 | 34 | 368.75 | 226.64 | 2539.4999 | 413.46 | 391.74 | 4389.4444 | 2.74 | 567.03 | 6.37 | 164.71 | 79.1999
1215.15 | 567.8789 | 18.042 | 567.1566 | 97.0037 | 17.248 | 264.655 | 1248.6769 | 138.8402 | 3.0287 | 564.2505 | 17.8715 | 567.1566 | 2.7655 | 14.9549 | 3.0678 | 20.0701 | -92.8417 | 36.7621 | 3.03 | 319.72 | 3.41 | 4.16 | 34 | 370.82 | 235.18 | 2571.8367 | 423.43 | 401.39 | 4389.4444 | 2.81 | 566.65 | 6.44 | 166.05 | 78.8101
1116.3385 | 568.4892 | 17.0823 | 567.6748 | 98.872 | 10.2845 | 263.9446 | 1161.6674 | 136.1197 | 3.7185 | 565.0684 | 16.9284 | 567.6748 | 2.5431 | 13.8463 | 2.8249 | 18.9423 | -92.9081 | 36.5756 | 2.8 | 320.17 | 3.56 | 4.1 | 34 | 363.08 | 220.96 | 2622.5337 | 390.95 | 369.83 | 4389.4444 | 2.59 | 567.45 | 6.06 | 162.93 | 76.8965
1085.2261 | 568.798 | 16.9707 | 566.9668 | 89.4696 | 7.0102 | 262.3203 | 1129.9638 | 133.4769 | 3.1787 | 565.2751 | 16.8321 | 566.9668 | 2.4721 | 13.4661 | 2.7474 | 18.7919 | -92.741 | 37.2129 | 2.72 | 319.56 | 3.25 | 3.76 | 34 | 361.13 | 209.64 | 2570.3998 | 378.66 | 358 | 4389.4444 | 2.52 | 566.91 | 5.99 | 160.93 | 78.9343
1052.1484 | 568.6772 | 16.7111 | 567.1968 | 89.1173 | 5.5224 | 260.9103 | 1095.4569 | 133.0293 | 3.3892 | 565.3396 | 16.5825 | 567.1968 | 2.3983 | 13.0187 | 2.6677 | 18.4516 | -92.9582 | 36.6681 | 2.64 | 319.73 | 3.27 | 3.79 | 33 | 360.1 | 204.02 | 2564.6045 | 366.96 | 346.44 | 4354.875 | 2.44 | 567.26 | 5.85 | 158.94 | 79.3228
1064.9071 | 568.4651 | 16.7216 | 566.2831 | 88.3372 | 5.4444 | 261.5303 | 1105.5925 | 133.0609 | 3.9305 | 564.9153 | 16.5936 | 566.2831 | 2.4275 | 13.1142 | 2.6989 | 18.4917 | -92.8149 | 36.976 | 2.66 | 320.67 | 3.88 | 4.38 | 36 | 362.42 | 206.54 | 2610.7508 | 369.15 | 344.52 | 4354.875 | 2.46 | 567.18 | 6.05 | 160.06 | 79.2634
1037.9019 | 568.5761 | 16.485 | 566.6875 | 83.3424 | 4.1227 | 261.1632 | 1087.3883 | 130.9235 | 3.9515 | 564.8044 | 16.3515 | 566.6875 | 2.3667 | 12.9161 | 2.6321 | 18.2302 | -92.8255 | 36.9767 | 2.59 | 320.6 | 4.11 | 4.63 | 37 | 359.36 | 200.5 | 2568.5487 | 360.5 | 339.94 | 4354.875 | 2.4 | 567.05 | 5.76 | 158.11 | 79.2421
989.8864 | 568.5555 | 16.0485 | 566.283 | 77.3946 | 2.751 | 258.6237 | 1039.9586 | 128.4808 | 3.8969 | 564.7731 | 15.9258 | 566.283 | 2.2576 | 12.2997 | 2.5128 | 17.7167 | -93.1814 | 36.0418 | 2.5 | 320.17 | 3.92 | 4.39 | 35 | 356.63 | 189.17 | 2523.2372 | 346.64 | 326.49 | 4354.875 | 2.3 | 566.23 | 5.62 | 155.93 | 80.4802
1033.2677 | 569.1454 | 16.392 | 566.9149 | 93.568 | 6.0898 | 260.554 | 1075.9837 | 130.5261 | 4.1193 | 565.2268 | 16.2661 | 566.9149 | 2.3449 | 12.7485 | 2.6209 | 18.0594 | -93.163 | 35.9935 | 2.58 | 321.2 | 3.86 | 4.31 | 35 | 355.32 | 195.54 | 2530.4655 | 357.18 | 336.52 | 4354.875 | 2.39 | 566.89 | 5.69 | 157.83 | 81.2661
1064.4421 | 568.8652 | 16.743 | 566.8764 | 98.2978 | 6.6609 | 262.3629 | 1108.7287 | 131.7864 | 3.9255 | 564.7131 | 16.6113 | 566.8764 | 2.4267 | 13.2043 | 2.6979 | 18.4848 | -92.9784 | 36.734 | 2.67 | 320.3 | 3.85 | 4.3 | 36 | 356.01 | 201.73 | 2496.5442 | 372.15 | 351.89 | 4354.875 | 2.47 | 567.2 | 5.89 | 159.94 | 80.9348
1030.9832 | 568.773 | 16.6619 | 566.2338 | 105.0567 | 6.2736 | 260.3197 | 1077.3129 | 134.7351 | 3.7709 | 565.1651 | 16.5413 | 566.2338 | 2.3499 | 12.7769 | 2.6154 | 18.3006 | -92.9587 | 37.1233 | 2.6 | 319.54 | 3.98 | 4.32 | 35 | 361.44 | 199.09 | 2545.3939 | 360.93 | 340.62 | 4354.875 | 2.4 | 566.72 | 5.82 | 158.91 | 79.736
942.7017 | 569.2071 | 15.6725 | 567.5253 | 88.3188 | 4.742 | 254.9095 | 994.983 | 135.9707 | 4.0447 | 565.5168 | 15.5773 | 567.5253 | 2.1524 | 11.6819 | 2.3971 | 17.2171 | -93.4202 | 36.1631 | 2.38 | 320.38 | 4.13 | 4.46 | 34 | 360.47 | 181.02 | 2546.8274 | 329.11 | 309.53 | 4354.875 | 2.19 | 567.21 | 5.4 | 154.12 | 80.5896
921.1179 | 568.8607 | 15.3542 | 567.0321 | 98.6726 | 1.2548 | 253.9887 | 974.3169 | 134.1637 | 4.2585 | 565.3244 | 15.2583 | 567.0321 | 2.1036 | 11.4352 | 2.3449 | 16.8528 | -93.3865 | 36.2787 | 2.33 | 320.95 | 4.23 | 4.53 | 35 | 357.46 | 178.86 | 2569.8217 | 322.92 | 303.1 | 4354.875 | 2.15 | 567.58 | 5.29 | 153.74 | 79.8137
984.1084 | 569.7629 | 16.013 | 567.4527 | 97.6837 | 2.7369 | 257.2507 | 1031.4489 | 133.6862 | 4.2097 | 566.0341 | 15.8935 | 567.4527 | 2.2461 | 12.2045 | 2.5008 | 17.6167 | -93.3579 | 36.2412 | 2.46 | 320.85 | 4.44 | 6.04 | 34 | 362.52 | 187.53 | 2537.2657 | 342.4 | 321.87 | 4354.875 | 2.27 | 567.64 | 5.52 | 155.54 | 81.0603
985.6273 | 568.4678 | 15.9362 | 567.2872 | 79.9478 | 3.889 | 257.389 | 1029.0457 | 133.3349 | 4.3478 | 564.9539 | 15.8123 | 567.2872 | 2.2488 | 12.2163 | 2.504 | 17.5715 | -93.1103 | 36.8613 | 2.48 | 320.5 | 4.56 | 6.81 | 33 | 363.27 | 187.73 | 2525.3782 | 344.34 | 323.73 | 4354.875 | 2.29 | 567.56 | 5.56 | 157 | 81.2146
950.5906 | 568.9717 | 15.6556 | 567.1163 | 88.4315 | 3.7714 | 255.5721 | 998.6123 | 131.0854 | 4.3067 | 565.4461 | 15.542 | 567.1163 | 2.1701 | 11.7666 | 2.4171 | 17.1789 | -93.3685 | 36.1936 | 2.39 | 321.15 | 4.67 | 6.43 | 30 | 359.34 | 180.99 | 2542.1346 | 330.64 | 310.05 | 4354.875 | 2.2 | 567.53 | 5.37 | 155.42 | 81.3258
931.7998 | 569.2411 | 15.4231 | 566.8585 | 83.0774 | 1.872 | 254.4952 | 984.11 | 131.86 | 4.0663 | 565.6833 | 15.3127 | 566.8585 | 2.1275 | 11.5561 | 2.3707 | 16.9399 | -93.4953 | 35.831 | 2.36 | 321.22 | 4.27 | 5.68 | 34 | 357.25 | 178.48 | 2535.171 | 326.7 | 306.59 | 4354.875 | 2.17 | 567.26 | 5.33 | 153.92 | 80.8371
910.3524 | 569.6636 | 15.2524 | 566.9892 | 87.9373 | 3.9725 | 253.319 | 962.7485 | 130.0043 | 4.5805 | 566.0771 | 15.1491 | 566.9892 | 2.0797 | 11.2706 | 2.3182 | 16.736 | -93.6942 | 35.2317 | 2.31 | 321.21 | 4.9 | 5.94 | 35 | 358.01 | 174.97 | 2539.6543 | 320.03 | 300.03 | 4354.875 | 2.12 | 567.58 | 5.26 | 152.52 | 80.8956
899.6582 | 569.4389 | 15.2618 | 567.1109 | 77.039 | 2.2544 | 252.5541 | 955.2494 | 129.7895 | 4.7822 | 566.0063 | 15.1583 | 567.1109 | 2.0556 | 11.1665 | 2.2917 | 16.7424 | -93.6519 | 35.353 | 2.27 | 321.21 | 5.02 | 6 | 33 | 358.33 | 173.28 | 2566.2736 | 314.08 | 294.05 | 4354.875 | 2.08 | 567.64 | 5.21 | 151.58 | 80.5847
901.9768 | 569.5759 | 15.0342 | 567.4456 | 82.6184 | 7.3908 | 252.4227 | 952.984 | 129.9803 | 4.5624 | 566.1254 | 14.9297 | 567.4456 | 2.0615 | 11.154 | 2.2974 | 16.4962 | -93.5414 | 35.7024 | 2.27 | 322.15 | 4.87 | 5.62 | 32 | 358.91 | 176.67 | 2615.0565 | 314.08 | 294.21 | 4354.875 | 2.09 | 567.93 | 5.12 | 154.49 | 79.6103
923.2227 | 569.5329 | 15.4293 | 567.7517 | 91.8364 | 4.9504 | 253.7983 | 972.8495 | 131.3343 | 4.5905 | 566.0341 | 15.3244 | 567.7517 | 2.1086 | 11.4304 | 2.3494 | 16.9233 | -93.3696 | 36.1596 | 2.32 | 321.4 | 4.92 | 5.41 | 33 | 360.69 | 178.99 | 2591.181 | 320.74 | 300.82 | 4354.875 | 2.13 | 567.64 | 5.27 | 155.05 | 80.2047
1013.1843 | 569.6108 | 16.4691 | 567.9182 | 100.9039 | 7.1107 | 258.6794 | 1059.2606 | 131.8068 | 4.178 | 566.0198 | 16.3389 | 567.9182 | 2.3114 | 12.5563 | 2.5707 | 18.0826 | -93.7284 | 34.8697 | 2.54 | 320.31 | 4.19 | 4.9 | 35 | 360.52 | 187.14 | 2435.804 | 355.09 | 334.58 | 4354.875 | 2.34 | 567.55 | 5.69 | 158.31 | 83.5629
1044.5509 | 569.4022 | 16.8007 | 567.8869 | 119.195 | 13.8343 | 260.4549 | 1086.0487 | 132.8262 | 4.1421 | 565.9142 | 16.6673 | 567.8869 | 2.3814 | 12.8864 | 2.6481 | 18.4036 | -93.3539 | 35.8787 | 2.63 | 320.31 | 3.81 | 4.53 | 34 | 361.66 | 189.14 | 2388.5198 | 365.54 | 344.85 | 4354.875 | 2.43 | 567.73 | 5.84 | 160.82 | 85.5767
974.183 | 568.2718 | 15.7372 | 565.782 | 92.4394 | 8.1792 | 256.6246 | 1021.552 | 134.6546 | 4.3125 | 564.9047 | 15.6108 | 565.782 | 2.2254 | 12.0813 | 2.4764 | 17.3347 | -93.3009 | 36.1423 | 2.42 | 320.04 | 4.68 | 5.21 | 36 | 357.77 | 175.87 | 2430.7854 | 334.69 | 315.08 | 4354.875 | 2.23 | 564.53 | 5.45 | 157.95 | 85.8007
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
1024.6224 | 569.5249 | 16.6527 | 567.6175 | 135.9705 | 5.2698 | 259.0619 | 1030.9346 | 136.9065 | 4.6033 | 566.0386 | 16.5259 | 567.6175 | 2.3364 | 12.7571 | 2.5988 | 18.2762 | -92.9084 | 36.672 | 2.56 | 319 | 4.52 | 5.79 | 33 | 371.04 | 198.4 | 2526.6714 | 356.88 | 336.36 | 4283.625 | 2.36 | 567.08 | 5.78 | 155.71 | 82.3309
1038.4939 | 569.1131 | 16.4509 | 566.8254 | 131.5531 | 9.282 | 259.4241 | 1033.0273 | 137.1946 | 4.5508 | 565.6457 | 16.3138 | 566.8254 | 2.3672 | 12.8731 | 2.6328 | 18.0816 | -92.9417 | 36.6985 | 2.6 | 320.66 | 4.31 | 5.83 | 34 | 375.93 | 197.42 | 2485.0085 | 361.8 | 340.31 | 4283.625 | 2.4 | 566.81 | 5.72 | 158.67 | 84.2337
975.0478 | 569.4264 | 15.8704 | 567.6344 | 132.3202 | 3.0975 | 256.5652 | 978.894 | 133.7465 | 4.7881 | 566.018 | 15.7581 | 567.6344 | 2.2252 | 12.1173 | 2.4776 | 17.4128 | -92.9899 | 36.6854 | 2.48 | 320.28 | 4.33 | 5.9 | 35 | 372.17 | 192.17 | 2550.8482 | 343.21 | 322.71 | 4283.625 | 2.28 | 567.41 | 5.51 | 156.19 | 81.4242
1144.6859 | 569.2411 | 17.6625 | 566.5668 | 132.7316 | 8.2467 | 265.2795 | 1144.0182 | 135.3225 | 3.8073 | 565.6215 | 17.5084 | 566.5668 | 2.6066 | 14.1986 | 2.8943 | 19.4734 | -92.7615 | 36.9232 | 2.87 | 319.54 | 3.34 | 5.74 | 33 | 373.23 | 218.78 | 2468.6444 | 401.69 | 379.63 | 4283.625 | 2.66 | 567.03 | 6.22 | 163.66 | 82.6051
929.6702 | 569.6233 | 15.6172 | 566.5685 | 119.6816 | 3.5036 | 254.3336 | 928.5801 | 133.7588 | 4.5255 | 566.1415 | 15.5178 | 566.5685 | 2.1237 | 11.5247 | 2.3663 | 17.0828 | -93.3203 | 35.7523 | 2.36 | 320.15 | 4.44 | 6.29 | 34 | 368.82 | 182.64 | 2558.492 | 326.4 | 305.79 | 4283.625 | 2.17 | 567.21 | 5.36 | 153.46 | 82.141
974.5208 | 569.5982 | 16.0823 | 567.3203 | 122.3209 | 1.9696 | 256.6406 | 976.401 | 136.3921 | 4.1433 | 566.1281 | 15.9718 | 567.3203 | 2.2236 | 12.1069 | 2.4763 | 17.6092 | -93.2459 | 36.1559 | 2.45 | 319.79 | 4.1 | 5.91 | 32 | 368.14 | 187 | 2507.0823 | 340.18 | 319.51 | 4283.625 | 2.25 | 567.59 | 5.53 | 153.2 | 83.5879
1062.8426 | 569.4049 | 16.7786 | 567.425 | 119.7498 | 5.2202 | 261.2404 | 1062.7892 | 137.1722 | 3.8904 | 565.9679 | 16.6425 | 567.425 | 2.4243 | 13.1948 | 2.6937 | 18.4786 | -93.1143 | 36.4291 | 2.66 | 320.27 | 3.76 | 5.97 | 34 | 371.6 | 201.56 | 2465.54 | 371.13 | 350.19 | 4283.625 | 2.46 | 568.25 | 5.85 | 159.23 | 84.0114
1126.9707 | 568.9305 | 17.5401 | 566.8157 | 127.8416 | 11.4937 | 264.3999 | 1143.1328 | 137.3092 | 3.605 | 565.3906 | 17.3756 | 566.8157 | 2.5665 | 14.1675 | 2.8518 | 19.3905 | -93.1919 | 36.2132 | 2.83 | 318.51 | 3.8 | 5.69 | 34 | 373.45 | 222.6 | 2538.2924 | 397.87 | 375.66 | 4283.625 | 2.61 | 567.48 | 6.18 | 161.72 | 79.7847
965.6555 | 569.2581 | 16.2207 | 565.9868 | 115.5022 | 4.1592 | 256.1566 | 966.8853 | 134.0132 | 4.166 | 565.9222 | 16.116 | 565.9868 | 2.2034 | 11.9436 | 2.4534 | 17.736 | -93.3133 | 36.1503 | 2.44 | 319.64 | 3.77 | 5.75 | 35 | 364.21 | 197.31 | 2659.6244 | 338.02 | 317.79 | 4283.625 | 2.24 | 567.12 | 5.57 | 152.78 | 78.6286
930.4916 | 569.0093 | 15.5145 | 566.837 | 101.6624 | 2.75 | 254.3724 | 926.6385 | 132.1086 | 4.6588 | 565.8739 | 15.4109 | 566.837 | 2.1253 | 11.5178 | 2.3661 | 17.0274 | -93.1834 | 36.5561 | 2.35 | 320.94 | 4.44 | 6.12 | 34 | 367.94 | 188.55 | 2645.2608 | 325.13 | 305.33 | 4283.625 | 2.16 | 567.15 | 5.34 | 154.41 | 79.7146
884.0168 | 569.3297 | 14.6248 | 567.6094 | 146.5589 | 11.1643 | 251.5459 | 870.2316 | 132.4843 | 4.3834 | 565.89 | 14.5308 | 567.6094 | 2.0206 | 10.865 | 2.2523 | 15.9163 | -93.3485 | 36.1141 | 2.23 | 323 | 4.2 | 5.53 | 32 | 362.73 | 175.92 | 2623.4127 | 306.61 | 287.25 | 4283.625 | 2.05 | 567.29 | 4.93 | 151.21 | 82.2375
853.8684 | 569.0514 | 13.9404 | 566.2419 | 135.891 | 9.4209 | 249.7402 | 843.2934 | 131.6929 | 4.5734 | 565.6331 | 13.8396 | 566.2419 | 1.9539 | 10.5404 | 2.1784 | 15.1909 | -93.5308 | 35.6453 | 2.16 | 324.01 | 4.41 | 5.62 | 33 | 359.69 | 170.32 | 2630.8489 | 296.84 | 277.32 | 4283.625 | 1.98 | 567.08 | 4.68 | 152.7 | 82.2308
853.8994 | 569.2367 | 13.9523 | 567.681 | 140.1908 | 7.692 | 249.756 | 842.9937 | 129.0945 | 4.3347 | 565.7835 | 13.8575 | 567.681 | 1.954 | 10.5385 | 2.1789 | 15.2051 | -93.5285 | 35.6164 | 2.16 | 323.88 | 4.31 | 5.54 | 30 | 358.49 | 170.33 | 2634.7086 | 296.37 | 276.93 | 4283.625 | 1.98 | 567.78 | 4.68 | 152.26 | 82.2026
902.8107 | 569.4344 | 14.934 | 567.4545 | 142.1228 | 8.0869 | 252.5951 | 892.9419 | 134.3189 | 4.2437 | 566.0833 | 14.8291 | 567.4545 | 2.0633 | 11.1182 | 2.2995 | 16.2435 | -93.3788 | 35.9458 | 2.29 | 322.57 | 4.45 | 5.68 | 34 | 361.49 | 182.71 | 2648.1513 | 315.46 | 295.55 | 4283.625 | 2.11 | 568.17 | 5.07 | 155.21 | 80.5336
955.6897 | 569.2116 | 15.766 | 567.3221 | 114.9131 | 5.7827 | 255.6405 | 951.9723 | 134.8283 | 3.9355 | 565.9992 | 15.6516 | 567.3221 | 2.1815 | 11.8385 | 2.4297 | 17.2456 | -93.3472 | 35.9075 | 2.41 | 321.07 | 4.53 | 5.96 | 34 | 366.3 | 196.15 | 2677.7776 | 334.23 | 313.78 | 4283.625 | 2.22 | 567.52 | 5.4 | 156.08 | 78.4936
990.9465 | 569.2993 | 16.1498 | 567.307 | 120.1724 | 6.757 | 257.5377 | 988.1329 | 135.2802 | 3.9385 | 566.0994 | 16.0206 | 567.307 | 2.2613 | 12.283 | 2.5156 | 17.7129 | -93.3591 | 35.7487 | 2.5 | 320.51 | 3.81 | 5.7 | 35 | 369.41 | 203.06 | 2662.0747 | 347.48 | 326.75 | 4283.625 | 2.3 | 567.44 | 5.58 | 157.02 | 78.3335
1069.8295 | 569.6296 | 16.8544 | 568.0113 | 107.1264 | 6.884 | 261.594 | 1070.4547 | 136.3475 | 3.9525 | 566.359 | 16.7067 | 568.0113 | 2.4379 | 13.2874 | 2.7101 | 18.6205 | -93.445 | 35.3146 | 2.68 | 320.52 | 3.24 | 5.49 | 34 | 373.58 | 214.07 | 2593.6068 | 374.87 | 353.56 | 4283.625 | 2.47 | 568.67 | 5.9 | 160.86 | 79.5623
974.2077 | 569.3906 | 16.0096 | 567.5101 | 116.9849 | 6.275 | 256.6585 | 975.8245 | 134.4449 | 4.0063 | 566.0959 | 15.888 | 567.5101 | 2.2226 | 12.1132 | 2.4746 | 17.5745 | -93.3464 | 35.746 | 2.47 | 320.39 | 3.47 | 5.44 | 36 | 365.73 | 196.36 | 2604.287 | 342.97 | 322.98 | 4283.625 | 2.27 | 568.16 | 5.54 | 156.24 | 79.7408
999.2167 | 569.5598 | 16.2749 | 567.7052 | 123.7732 | 5.1035 | 257.9989 | 999.5391 | 135.7632 | 3.8681 | 566.2793 | 16.1458 | 567.7052 | 2.2795 | 12.3995 | 2.5372 | 17.863 | -93.173 | 36.149 | 2.52 | 320.39 | 3.19 | 5.34 | 35 | 367.38 | 200.65 | 2608.447 | 349.78 | 329.51 | 4283.625 | 2.32 | 568.35 | 5.64 | 157.67 | 79.873
958.1788 | 569.3996 | 15.6396 | 566.923 | 119.1392 | 6.5467 | 255.8734 | 957.6486 | 133.9423 | 4.0513 | 566.137 | 15.5179 | 566.923 | 2.1872 | 11.8901 | 2.4352 | 17.1654 | -93.2437 | 36.0331 | 2.42 | 321.39 | 3.66 | 5.38 | 34 | 365.88 | 195.13 | 2653.6199 | 334.92 | 314.99 | 4283.625 | 2.23 | 567.84 | 5.39 | 155.27 | 79.1319
1023.5716 | 569.1588 | 16.5018 | 566.266 | 123.4444 | 4.5247 | 259.3574 | 1023.2225 | 135.6214 | 4.0664 | 565.8309 | 16.3736 | 566.266 | 2.334 | 12.6847 | 2.5967 | 18.137 | -93.0326 | 36.424 | 2.57 | 320.29 | 3.69 | 5.42 | 32 | 369.64 | 202.8 | 2579.8686 | 357.03 | 336.73 | 4283.625 | 2.37 | 567.44 | 5.72 | 157.91 | 80.6078
1043.9557 | 569.4452 | 16.5397 | 567.3337 | 122.59 | 7.7872 | 260.2443 | 1039.1523 | 137.0528 | 4.0935 | 566.0815 | 16.3983 | 567.3337 | 2.38 | 12.9392 | 2.6459 | 18.2033 | -93.0246 | 36.3719 | 2.61 | 321 | 4.01 | 5.79 | 34 | 373.5 | 207.22 | 2588.3617 | 363.37 | 342.94 | 4283.625 | 2.41 | 568.11 | 5.75 | 158.25 | 80.4849
1016.3678 | 569.3485 | 16.4333 | 567.5664 | 118.1559 | 5.3833 | 258.9188 | 1013.1861 | 136.2393 | 4.2058 | 566.0932 | 16.2989 | 567.5664 | 2.3192 | 12.5973 | 2.5788 | 18.0232 | -92.9719 | 36.5518 | 2.55 | 320.48 | 4.3 | 6.18 | 34 | 371.95 | 202.18 | 2598.9176 | 353.58 | 333.24 | 4283.625 | 2.35 | 568.35 | 5.7 | 158.64 | 80.4671
914.283 | 569.6027 | 15.2352 | 566.8514 | 110.8385 | 4.2985 | 253.4832 | 911.0822 | 136.627 | 4.4335 | 566.4825 | 15.1281 | 566.8514 | 2.0886 | 11.3562 | 2.3281 | 16.6687 | -93.3946 | 35.5139 | 2.32 | 321.47 | 4.43 | 6.49 | 34 | 370.08 | 183.47 | 2617.9769 | 320.08 | 300.2 | 4283.625 | 2.13 | 567.91 | 5.21 | 152.82 | 80.6909
939.7941 | 569.1283 | 15.5483 | 567.2021 | 117.565 | 3.4493 | 254.704 | 934.3558 | 136.0215 | 4.4702 | 566.026 | 15.4381 | 567.2021 | 2.1451 | 11.6209 | 2.3901 | 17.0044 | -93.2788 | 35.7949 | 2.37 | 321.7 | 4.49 | 6.56 | 34 | 369.44 | 186.9 | 2610.4846 | 326.76 | 306.69 | 4283.625 | 2.18 | 568 | 5.3 | 154.58 | 81.1997
912.8291 | 569.7585 | 14.9375 | 567.4949 | 134.0654 | 12.3968 | 253.091 | 908.1604 | 137.904 | 4.2988 | 566.5165 | 14.8221 | 567.4949 | 2.0861 | 11.2989 | 2.3237 | 16.307 | -93.1493 | 36.2405 | 2.31 | 322.89 | 4.26 | 6.12 | 35 | 372.23 | 183.53 | 2639.4954 | 317.57 | 297.85 | 4283.625 | 2.12 | 568.05 | 5.09 | 154.17 | 80.9077
927.1997 | 569.0442 | 14.9121 | 567.0885 | 129.3621 | 13.1616 | 253.9441 | 917.3991 | 139.5839 | 4.1392 | 565.7271 | 14.7964 | 567.0885 | 2.1186 | 11.4544 | 2.3591 | 16.337 | -93.0271 | 36.463 | 2.34 | 323.45 | 4.5 | 5.89 | 35 | 368.7 | 187.15 | 2659.4142 | 321 | 301.45 | 4283.625 | 2.15 | 568.29 | 5.07 | 155.82 | 80.6763
1056.6834 | 569.4721 | 16.7759 | 567.979 | 133.4792 | 15.4679 | 261.0189 | 1046.2773 | 141.5967 | 3.7074 | 566.0645 | 16.6426 | 567.979 | 2.4098 | 13.0266 | 2.6788 | 18.3843 | -92.8344 | 36.8176 | 2.65 | 320.95 | 3.88 | 5.39 | 37 | 370.34 | 211.54 | 2618.3485 | 366.24 | 346.08 | 4283.625 | 2.45 | 568.52 | 5.8 | 161.21 | 80.167
1021.16 | 568.8634 | 16.475 | 567.6121 | 133.6476 | 13.5399 | 259.1641 | 1015.1376 | 142.1268 | 3.5599 | 565.7164 | 16.3477 | 567.6121 | 2.33 | 12.6364 | 2.5904 | 18.0348 | -92.818 | 36.7816 | 2.56 | 320.71 | 3.48 | 5.19 | 29 | 368.43 | 205.16 | 2632.2476 | 353.89 | 333.87 | 4283.625 | 2.36 | 568.11 | 5.67 | 159.73 | 79.8765
1126.5864 | 568.969 | 17.2381 | 566.9686 | 116.3832 | 9.4063 | 264.552 | 1120.1055 | 143.3872 | 3.368 | 565.6958 | 17.0687 | 566.9686 | 2.5666 | 13.9742 | 2.8501 | 19.0388 | -92.515 | 37.2649 | 2.83 | 320.95 | 2.82 | 5.3 | 36 | 375.12 | 217.85 | 2505.2019 | 393.2 | 372.5 | 4283.625 | 2.62 | 567.7 | 6.1 | 163.64 | 82.0851
1011.4608 | 569.4756 | 16.2177 | 567.3391 | 99.5973 | 5.1805 | 258.7462 | 1013.1642 | 138.6018 | 3.7152 | 566.1048 | 16.0832 | 567.3391 | 2.307 | 12.5863 | 2.5661 | 17.8389 | -92.9191 | 36.4103 | 2.55 | 320.92 | 3.44 | 5.31 | 36 | 367.61 | 200.32 | 2575.0083 | 353.39 | 333.24 | 4283.625 | 2.35 | 568.01 | 5.67 | 158.55 | 80.7678
937.7234 | 569.1462 | 15.3714 | 567.1252 | 101.9103 | 4.3345 | 254.821 | 937.6723 | 136.3693 | 4.0179 | 565.7871 | 15.2602 | 567.1252 | 2.1411 | 11.682 | 2.3847 | 16.8981 | -92.84 | 36.7476 | 2.37 | 321.66 | 3.87 | 5.46 | 33 | 365.74 | 187.91 | 2593.0515 | 325.56 | 306.06 | 4223.4545 | 2.18 | 568.03 | 5.28 | 155.26 | 81.645
879.9158 | 569.3503 | 14.6808 | 567.5888 | 80.5809 | 5.3119 | 251.6351 | 878.1265 | 134.2198 | 4.1629 | 566.1218 | 14.577 | 567.5888 | 2.0112 | 10.935 | 2.2419 | 16.139 | -93.1885 | 35.8663 | 2.23 | 322.61 | 4.48 | 6.13 | 34 | 364.74 | 176.73 | 2606.7302 | 305.73 | 286.34 | 4223.4545 | 2.04 | 567.24 | 5.02 | 151.06 | 82.0247
864.6742 | 569.2197 | 14.5156 | 566.6705 | 95.5118 | 5.362 | 250.7071 | 860.9224 | 137.4661 | 3.7752 | 566.1173 | 14.4119 | 566.6705 | 1.9775 | 10.7524 | 2.2053 | 15.9099 | -93.1946 | 35.8475 | 2.19 | 322.78 | 4.35 | 6.45 | 34 | 366.83 | 180.93 | 2724.824 | 299.66 | 280.44 | 4223.4545 | 2 | 566.46 | 4.93 | 151.62 | 78.8409
901.9211 | 569.5571 | 15.0715 | 567.4618 | 98.036 | 4.5247 | 252.8016 | 899.1177 | 137.9603 | 3.8596 | 566.4002 | 14.964 | 567.4618 | 2.0605 | 11.2078 | 2.2968 | 16.5026 | -92.9443 | 36.3857 | 2.28 | 322.22 | 4.13 | 6.15 | 31 | 371.06 | 185.06 | 2669.0087 | 312.21 | 292.84 | 4223.4545 | 2.09 | 567.15 | 5.13 | 153.9 | 80.0514
884.6677 | 569.3252 | 14.6683 | 567.4537 | 89.5644 | 2.4215 | 251.7777 | 878.3548 | 137.0887 | 4.1163 | 566.2068 | 14.562 | 567.4537 | 2.0226 | 10.9642 | 2.2552 | 16.1028 | -93.2064 | 36.0714 | 2.24 | 323.29 | 4.23 | 6.17 | 31 | 368.71 | 179.33 | 2638.0777 | 306.92 | 287.1 | 4223.4545 | 2.05 | 567.69 | 5.01 | 151.83 | 81.3435
819.5163 | 567.5899 | 13.9392 | 565.5894 | 89.4193 | 2.9391 | 247.6205 | 823.0922 | 133.9302 | 4.4617 | 564.6702 | 13.8448 | 565.5894 | 1.8739 | 10.2187 | 2.0924 | 15.256 | -93.395 | 35.7775 | 2.07 | 322.24 | 4.78 | 6.41 | 32 | 364.16 | 164.59 | 2617.1394 | 283.63 | 265.61 | 4223.4545 | 1.89 | 566.58 | 4.69 | 148.84 | 82.2909
835.0371 | 568.501 | 14.1647 | 566.0056 | 83.6172 | 2.9421 | 248.4641 | 839.0169 | 135.7051 | 4.4127 | 565.3987 | 14.0653 | 566.0056 | 1.9088 | 10.4378 | 2.1308 | 15.5481 | -92.9817 | 35.6261 | 2.11 | 321.9 | 4.33 | 6.19 | 33 | 365.66 | 156.73 | 2454.8193 | 288.1 | 269.65 | 4223.4545 | 1.93 | 566.71 | 4.82 | 148.09 | 87.9927
880.2127 | 568.6612 | 14.3878 | 566.4182 | 83.3804 | 4.613 | 251.0135 | 880.291 | 139.7022 | 4.2391 | 565.2707 | 14.2753 | 566.4182 | 2.0111 | 10.9667 | 2.2418 | 15.8626 | -92.6724 | 35.6866 | 2.23 | 322.31 | 4.11 | 6.09 | 34 | 371.37 | 164.82 | 2442.6619 | 303.58 | 284.98 | 4223.4545 | 2.04 | 566.77 | 4.96 | 152.11 | 87.9742
877.3243 | 569.2948 | 14.6406 | 566.7995 | 100.4264 | 4.485 | 251.4913 | 879.2617 | 138.4551 | 4.1863 | 566.0762 | 14.5363 | 566.7995 | 2.006 | 10.9595 | 2.2363 | 16.0569 | -92.6779 | 35.6698 | 2.22 | 322.27 | 4.32 | 5.95 | 33 | 366.89 | 168.56 | 2510.1565 | 302.93 | 283.61 | 4223.4545 | 2.04 | 566.56 | 4.99 | 150.37 | 85.5331
882.8792 | 569.3843 | 14.6502 | 567.3892 | 109.006 | 3.6547 | 251.6819 | 880.2448 | 135.3708 | 4.0458 | 566.2811 | 14.5472 | 567.3892 | 2.0184 | 10.9688 | 2.2498 | 16.0284 | -92.7904 | 35.6837 | 2.24 | 323.07 | 4.5 | 5.91 | 32 | 364.7 | 178.44 | 2635.2655 | 305.04 | 285.98 | 4223.4545 | 2.05 | 567.45 | 4.99 | 153 | 81.4662
814.8727 | 568.5492 | 13.7203 | 566.3949 | 98.1431 | 6.3722 | 247.0306 | 812.9326 | 133.8555 | 4.5313 | 565.4837 | 13.624 | 566.3949 | 1.8638 | 10.1348 | 2.0807 | 15.025 | -92.659 | 35.6765 | 2.06 | 323.69 | 4.83 | 6.53 | 33 | 366.91 | 162.33 | 2620.3691 | 279.68 | 261.64 | 4223.4545 | 1.89 | 566.19 | 4.62 | 150.16 | 83.3622
880.4365 | 569.6117 | 14.4401 | 567.4107 | 103.4555 | 8.8873 | 251.4452 | 872.9047 | 134.1487 | 4.0035 | 566.4422 | 14.3327 | 567.4107 | 2.0133 | 10.9167 | 2.2437 | 15.856 | -92.4569 | 36.4934 | 2.22 | 323.9 | 4.53 | 6.56 | 31 | 368.64 | 167 | 2494.4013 | 301.67 | 282.76 | 4223.4545 | 2.04 | 566.67 | 4.9 | 153.55 | 87.0295
882.8296 | 569.3288 | 14.3659 | 566.718 | 104.5038 | 6.4236 | 251.7883 | 878.9302 | 133.8034 | 3.9142 | 565.8909 | 14.2557 | 566.718 | 2.0181 | 10.9747 | 2.2498 | 15.7913 | -92.5372 | 36.3423 | 2.23 | 323.88 | 4.4 | 6.35 | 33 | 366.92 | 165.92 | 2468.0575 | 302.98 | 283.93 | 4223.4545 | 2.04 | 565.82 | 4.88 | 152.84 | 87.5768
902.5968 | 568.6119 | 14.6936 | 566.5238 | 103.5215 | 5.5774 | 253.4386 | 901.3689 | 135.1286 | 4.0884 | 564.9055 | 14.5743 | 566.5238 | 2.0631 | 11.2129 | 2.2991 | 16.141 | -92.6303 | 36.1834 | 2.27 | 323.11 | 4.26 | 6.25 | 34 | 368.34 | 169.68 | 2470.5615 | 309.11 | 290.07 | 4223.4545 | 2.08 | 565.7 | 5.03 | 152.55 | 87.15
1007.1552 | 568.4221 | 15.7118 | 566.3027 | 97.9329 | 17.7626 | 258.1052 | 1000.4705 | 143.2135 | 3.6733 | 564.9458 | 15.5718 | 566.3027 | 2.2981 | 12.4544 | 2.5564 | 17.3936 | -92.3742 | 36.7579 | 2.52 | 322.56 | 3.74 | 5.8 | 33 | 375.29 | 186.9 | 2438.7915 | 344.46 | 323.67 | 4223.4545 | 2.32 | 565.91 | 5.44 | 157.3 | 88.0357
894.3173 | 568.8876 | 14.8019 | 566.1032 | 86.9613 | 6.1076 | 252.6823 | 890.1916 | 140.8114 | 4.2223 | 565.5812 | 14.6939 | 566.1032 | 2.0441 | 11.1 | 2.2781 | 16.3058 | -92.4794 | 36.1705 | 2.27 | 322.25 | 4.05 | 5.7 | 34 | 370.21 | 170.49 | 2485.0109 | 309.1 | 289.76 | 4223.4545 | 2.08 | 566.39 | 5.07 | 153.17 | 86.3246
869.7764 | 569.2268 | 14.3489 | 566.7582 | 100.4454 | 3.9559 | 251.0099 | 869.1509 | 140.4691 | 4.2174 | 565.95 | 14.2437 | 566.7582 | 1.9889 | 10.8229 | 2.2168 | 15.7832 | -92.3923 | 36.2846 | 2.21 | 322.77 | 4.25 | 5.94 | 32 | 367.48 | 164.34 | 2475.5065 | 299.93 | 280.38 | 4223.4545 | 2.02 | 567.2 | 4.9 | 151.37 | 87.207
1010.3759 | 569.1194 | 15.7568 | 566.539 | 95.0951 | 10.6966 | 257.3607 | 1002.3586 | 142.477 | 4.0366 | 565.6448 | 15.6204 | 566.539 | 2.3058 | 12.4334 | 2.5643 | 17.4608 | -92.4229 | 36.4118 | 2.54 | 322.22 | 4.1 | 6.23 | 32 | 377.67 | 185.36 | 2400.3052 | 347.48 | 326.15 | 4223.4545 | 2.34 | 566.62 | 5.5 | 157.33 | 88.9528
888.2882 | 568.8831 | 14.7543 | 565.6225 | 94.8965 | 2.2814 | 252.0628 | 891.3177 | 131.1711 | 4.0319 | 565.6868 | 14.6452 | 565.6225 | 2.0297 | 11.0335 | 2.2631 | 16.2028 | -92.3401 | 36.0637 | 2.24 | 321.91 | 4.12 | 5.76 | 33 | 363.27 | 165.65 | 2458.0678 | 304.01 | 284.62 | 4223.4545 | 2.05 | 566.14 | 5.01 | 147.25 | 87.9518
907.7517 | 568.901 | 14.7387 | 566.5479 | 107.7674 | 7.1864 | 252.9755 | 905.1673 | 132.0394 | 4.0358 | 565.634 | 14.6255 | 566.5479 | 2.0745 | 11.219 | 2.3115 | 16.2064 | -92.2811 | 36.3959 | 2.3 | 323.05 | 4.08 | 5.46 | 32 | 368.82 | 171.04 | 2468.6613 | 312.46 | 292.62 | 4223.4545 | 2.11 | 567.24 | 5.06 | 152.96 | 87.3562
889.4166 | 568.5465 | 14.4829 | 565.8829 | 111.8085 | 4.404 | 252.1346 | 885.4782 | 130.5344 | 3.6279 | 565.4192 | 14.374 | 565.8829 | 2.0337 | 11.019 | 2.2668 | 15.8855 | -92.2613 | 36.2152 | 2.24 | 323.27 | 4.26 | 5.14 | 33 | 361.6 | 167.15 | 2476.6714 | 304.34 | 285.04 | 4223.4545 | 2.06 | 567 | 4.91 | 152.38 | 87.594
876.7788 | 568.6719 | 14.2225 | 566.4351 | 114.9132 | 4.4908 | 251.397 | 874.7251 | 132.2332 | 3.6436 | 565.3915 | 14.1173 | 566.4351 | 2.0051 | 10.8785 | 2.2355 | 15.6208 | -92.3408 | 35.9147 | 2.23 | 323.24 | 4.2 | 5.22 | 32 | 363.71 | 169.03 | 2522.9379 | 302.23 | 282.96 | 4223.4545 | 2.04 | 566.87 | 4.85 | 151.81 | 85.5013
870.5885 | 568.9001 | 14.1921 | 566.7663 | 109.426 | 5.5344 | 251.0457 | 869.9766 | 133.2955 | 3.473 | 565.6537 | 14.0823 | 566.7663 | 1.9909 | 10.8192 | 2.2192 | 15.5873 | -92.3186 | 36.0614 | 2.21 | 323.49 | 4.2 | 5.09 | 33 | 364.63 | 165.84 | 2498.5471 | 299.17 | 280.33 | 4223.4545 | 2.02 | 567.08 | 4.83 | 152.36 | 86.501
892.8542 | 569.1293 | 14.7407 | 567.2416 | 105.6793 | 4.8603 | 252.1075 | 889.189 | 132.7777 | 3.4964 | 565.805 | 14.6347 | 567.2416 | 2.0409 | 11.0474 | 2.2743 | 16.1425 | -92.4507 | 35.9263 | 2.25 | 322.7 | 3.73 | 5.07 | 30 | 364.66 | 165.39 | 2437.935 | 305.54 | 286.52 | 4223.4545 | 2.06 | 567.2 | 4.98 | 153.02 | 88.8915
964.4342 | 568.6038 | 15.4433 | 566.4467 | 113.1127 | 6.804 | 256.1399 | 961.2258 | 132.202 | 3.7301 | 565.2984 | 15.3188 | 566.4467 | 2.2019 | 11.9254 | 2.4515 | 16.9693 | -92.3786 | 36.7643 | 2.44 | 322.2 | 3.53 | 5.12 | 33 | 367.29 | 175.55 | 2368.6264 | 332.85 | 313.02 | 4223.4545 | 2.24 | 567.25 | 5.33 | 156.95 | 89.8659
926.4309 | 568.5474 | 15.1752 | 566.334 | 123.6803 | 7.4018 | 254.1816 | 919.442 | 132.1706 | 3.6301 | 565.3646 | 15.0671 | 566.334 | 2.1169 | 11.4348 | 2.3577 | 16.5822 | -92.5165 | 36.3973 | 2.33 | 322.2 | 4.06 | 5.05 | 32 | 364.11 | 172.07 | 2432.487 | 318.38 | 298.76 | 4223.4545 | 2.15 | 567.04 | 5.16 | 154.75 | 88.3774
884.3794 | 568.7829 | 14.2957 | 566.9802 | 120.8552 | 9.8733 | 251.8793 | 878.0993 | 132.3591 | 3.8792 | 565.4398 | 14.1885 | 566.9802 | 2.0222 | 10.9381 | 2.2536 | 15.6674 | -92.4355 | 36.4803 | 2.24 | 323.55 | 4.35 | 5.05 | 30 | 363.96 | 168.01 | 2496.5085 | 303.58 | 284.23 | 4223.4545 | 2.05 | 567.41 | 4.85 | 153.23 | 86.965
879.0912 | 568.722 | 13.9812 | 567.0303 | 130.4554 | 7.3406 | 251.6488 | 872.8239 | 130.6411 | 3.7856 | 565.2993 | 13.8671 | 567.0303 | 2.0101 | 10.8921 | 2.241 | 15.3441 | -92.3341 | 36.2969 | 2.23 | 324.76 | 3.95 | 4.86 | 32 | 361.01 | 168.04 | 2514.916 | 301.72 | 282.2 | 4223.4545 | 2.04 | 567.42 | 4.76 | 153.34 | 86.5036
917.017 | 569.3619 | 14.8023 | 566.8835 | 127.6435 | 5.0216 | 253.8553 | 911.7702 | 128.6716 | 3.4786 | 565.9482 | 14.688 | 566.8835 | 2.0953 | 11.3353 | 2.3345 | 16.2044 | -92.4352 | 36.4355 | 2.32 | 323.05 | 3.52 | 4.74 | 29 | 360.46 | 172.27 | 2458.6034 | 315.59 | 295.93 | 4223.4545 | 2.13 | 567.02 | 5.05 | 153.63 | 87.4945
944.4716 | 568.9771 | 15.2485 | 566.6088 | 132.3733 | 8.0907 | 255.3299 | 934.6656 | 128.7867 | 3.3609 | 565.5911 | 15.1316 | 566.6088 | 2.1575 | 11.6231 | 2.4023 | 16.6347 | -92.2641 | 37.3923 | 2.38 | 322.57 | 3.52 | 4.52 | 33 | 360.59 | 177.98 | 2469.1733 | 323.96 | 304.43 | 4223.4545 | 2.19 | 566.9 | 5.19 | 155.65 | 87.1086
871.9989 | 568.8411 | 14.4457 | 566.6365 | 98.9248 | 2.9092 | 251.2238 | 872.9975 | 127.1516 | 3.7626 | 565.5553 | 14.3417 | 566.6365 | 1.9926 | 10.8305 | 2.2223 | 15.8329 | -92.56 | 36.2535 | 2.21 | 322.83 | 4.02 | 4.74 | 29.5 | 358.96 | 161.43 | 2484.1112 | 300.8 | 281.84 | 4337 | 2.03 | 567.04 | 4.9 | 151.35 | 86.5178
879.7298 | 568.2342 | 14.442 | 565.6575 | 93.4156 | 3.4118 | 251.6605 | 880.2065 | 126.1413 | 3.9781 | 564.9485 | 14.3356 | 565.6575 | 2.0119 | 10.9363 | 2.2425 | 15.8578 | -92.6798 | 35.9631 | 2.22 | 322.28 | 4.07 | 5.03 | 28 | 358.77 | 156.45 | 2386.5627 | 303.12 | 284.31 | 4337 | 2.04 | 565.66 | 4.9 | 149.45 | 89.9473
909.2148 | 567.6667 | 15.0588 | 565.72 | 115.9037 | 3.6837 | 253.2919 | 907.1403 | 124.9755 | 4.1772 | 564.2951 | 14.951 | 565.72 | 2.0784 | 11.2642 | 2.3152 | 16.4417 | -92.6146 | 35.7103 | 2.3 | 321.08 | 3.92 | 5.22 | 27.5 | 357.62 | 161.88 | 2385.2469 | 313.79 | 294.34 | 4337 | 2.11 | 566.22 | 5.11 | 153.96 | 89.704
935.9875 | 567.4769 | 15.4784 | 565.9823 | 130.4212 | 5.1399 | 254.7251 | 931.1083 | 126.1303 | 3.7484 | 564.1063 | 15.3676 | 565.9823 | 2.138 | 11.5648 | 2.3813 | 16.8353 | -92.7576 | 35.7782 | 2.36 | 320.48 | 4.15 | 5.17 | 28.5 | 356.33 | 163.51 | 2334.1657 | 323.63 | 303.81 | 4337 | 2.17 | 565.95 | 5.24 | 154.65 | 91.1203
894.4227 | 568.3558 | 14.8017 | 566.487 | 109.5917 | 6.0479 | 252.4213 | 891.7995 | 124.2552 | 3.7746 | 564.6916 | 14.6922 | 566.487 | 2.0442 | 11.082 | 2.2778 | 16.1583 | -92.927 | 35.2749 | 2.26 | 321.77 | 4.4 | 5.16 | 27 | 357.33 | 157.59 | 2360.2854 | 308.97 | 289.57 | 4337 | 2.07 | 566.1 | 5 | 152.96 | 90.7969
913.2011 | 567.8618 | 14.7763 | 566.3581 | 131.2569 | 5.7645 | 253.4155 | 906.7582 | 124.856 | 4.2236 | 564.4509 | 14.6649 | 566.3581 | 2.0873 | 11.3016 | 2.3249 | 16.1552 | -92.5744 | 35.6412 | 2.3 | 322.77 | 4.44 | 5.19 | 27.5 | 357.07 | 162.63 | 2393.9392 | 314.09 | 294.63 | 4337 | 2.12 | 566.7 | 4.99 | 153.46 | 89.8257
927.1563 | 568.2744 | 15.07 | 566.1076 | 134.4901 | 5.7928 | 254.2537 | 925.0304 | 125.021 | 3.8398 | 564.8411 | 14.9608 | 566.1076 | 2.1194 | 11.4823 | 2.36 | 16.4596 | -92.8903 | 36.3756 | 2.34 | 321.75 | 3.67 | 4.83 | 29.5 | 355.72 | 164.02 | 2363.3833 | 320.72 | 300.99 | 4337 | 2.15 | 566.05 | 5.13 | 152.53 | 90.1362
915.8917 | 567.6345 | 14.8796 | 565.6762 | 129.3182 | 6.647 | 253.5592 | 910.984 | 124.2937 | 3.9785 | 564.3918 | 14.7721 | 565.6762 | 2.0926 | 11.3301 | 2.3314 | 16.2586 | -92.9344 | 37.2988 | 2.31 | 322.3 | 4.03 | 5.24 | 30.5 | 356.22 | 162.11 | 2365.4109 | 316.73 | 297.23 | 4337 | 2.13 | 566.35 | 5.04 | 153.34 | 90.3261
991.5169 | 568.2055 | 15.8327 | 567.0446 | 150.2573 | 13.8174 | 257.5673 | 986.7126 | 126.9414 | 3.5331 | 564.5717 | 15.7069 | 567.0446 | 2.2639 | 12.2322 | 2.5182 | 17.2563 | -92.9336 | 37.1169 | 2.48 | 321.16 | 3.68 | 5.07 | 29 | 358.73 | 178.24 | 2404.2139 | 341.66 | 321.53 | 4337 | 2.29 | 566.7 | 5.39 | 158.14 | 88.4496
984.8462 | 567.9621 | 15.8552 | 565.7084 | 128.1183 | 5.424 | 257.452 | 984.4757 | 130.2795 | 3.521 | 564.4133 | 15.7287 | 565.7084 | 2.2484 | 12.2101 | 2.5018 | 17.3543 | -93.0508 | 36.8242 | 2.48 | 320.54 | 3.43 | 4.58 | 29.5 | 362.35 | 177.37 | 2387.8001 | 342.09 | 322.16 | 4337 | 2.28 | 566.49 | 5.44 | 157 | 87.9901
1021.4886 | 567.3776 | 16.2674 | 565.814 | 130.6109 | 12.6974 | 259.159 | 1021.3491 | 129.8431 | 3.6343 | 563.9828 | 16.14 | 565.814 | 2.3316 | 12.6034 | 2.5912 | 17.8272 | -93.0161 | 36.8509 | 2.57 | 320.49 | 3.81 | 4.74 | 28 | 364.31 | 178.6 | 2316.9759 | 354.46 | 334.31 | 4337 | 2.37 | 566.36 | 5.58 | 158.32 | 90.3705
1030.7135 | 567.817 | 16.5272 | 565.8695 | 117.3046 | 7.8874 | 259.8029 | 1031.1461 | 128.5726 | 3.4417 | 564.1251 | 16.3939 | 565.8695 | 2.3511 | 12.7648 | 2.613 | 18.1017 | -93.09 | 36.6255 | 2.58 | 319.39 | 3.73 | 4.65 | 28 | 362.25 | 177.27 | 2285.2981 | 356.35 | 336.42 | 4337 | 2.38 | 566.33 | 5.7 | 159.11 | 91.5419
1100.1763 | 567.5763 | 16.8862 | 565.831 | 133.4567 | 16.4201 | 262.9341 | 1105.4892 | 127.519 | 3.3988 | 563.9479 | 16.7314 | 565.831 | 2.5061 | 13.6296 | 2.7839 | 18.5843 | -92.8945 | 36.9911 | 2.73 | 320.17 | 3.35 | 4.91 | 29 | 365.67 | 192.94 | 2342.6114 | 378.05 | 357.2 | 4337 | 2.52 | 566.22 | 5.84 | 161.57 | 89.3792
1138.9513 | 567.7329 | 17.1074 | 566.7573 | 150.74 | 15.2601 | 264.4761 | 1145.5237 | 128.3238 | 3.3266 | 564.2576 | 16.9307 | 566.7573 | 2.5935 | 14.1949 | 2.8789 | 18.856 | -92.8644 | 36.9845 | 2.64 | 319.85 | 3.33 | 4.53 | 28.5 | 355.83 | 190.1 | 2386.0843 | 366.46 | 345.53 | 4337 | 2.45 | 566.3 | 5.78 | 159.44 | 93.3023
917.1967 | 567.9746 | 14.8992 | 564.818 | 100.5807 | 3.047 | 253.8399 | 918.8581 | 128.7355 | 3.7954 | 564.458 | 14.7803 | 564.818 | 2.0961 | 11.4359 | 2.3342 | 16.3847 | -93.1638 | 36.5966 | 2.32 | 321.29 | 4.21 | 4.88 | 27.5 | 357.4 | 163.23 | 2361.1784 | 319.6 | 299.82 | 4337 | 2.13 | 565.27 | 5.12 | 151.94 | 89.3762
1059.7863 | 568.363 | 16.5933 | 566.9739 | 113.2294 | 12.7132 | 261.315 | 1056.6883 | 129.1282 | 3.3526 | 564.7462 | 16.4437 | 566.9739 | 2.4159 | 13.1109 | 2.6849 | 18.2365 | -92.8899 | 37.0568 | 2.65 | 320.27 | 3.4 | 4.55 | 26 | 362.78 | 186.57 | 2337.1771 | 366.94 | 346.21 | 4337 | 2.45 | 566.61 | 5.75 | 160.05 | 89.4978
1066.24 | 568.2726 | 16.6129 | 566.9256 | 149.6833 | 18.9733 | 261.5101 | 1058.2013 | 127.2798 | 3.4686 | 564.8348 | 16.4662 | 566.9256 | 2.4315 | 13.1207 | 2.7004 | 18.1813 | -92.8358 | 37.1384 | 2.67 | 321.15 | 3.49 | 4.8 | 26 | 362.77 | 189.92 | 2369.0838 | 368.57 | 347.68 | 4337 | 2.47 | 567.1 | 5.73 | 161.42 | 88.882
1007.49 | 568.1903 | 16.0791 | 566.4843 | 156.9901 | 11.853 | 258.5301 | 1002.2259 | 127.8767 | 3.5583 | 564.7865 | 15.9481 | 566.4843 | 2.2988 | 12.4276 | 2.5566 | 17.53 | -92.8913 | 37.0641 | 2.54 | 321.09 | 3.31 | 5.33 | 27.5 | 358.3 | 183.63 | 2422.3722 | 348.81 | 328.77 | 4337 | 2.34 | 566.95 | 5.51 | 159.18 | 87.1705
952.8813 | 568.6226 | 15.5319 | 566.9757 | 152.2997 | 9.7856 | 255.6716 | 948.3098 | 126.7248 | 3.7141 | 565.0183 | 15.4179 | 566.9757 | 2.1773 | 11.7387 | 2.4226 | 16.8858 | -93.0675 | 36.7208 | 2.41 | 321.29 | 3.58 | 4.59 | 27 | 355.26 | 172.7 | 2412.1603 | 330.12 | 310.51 | 4337 | 2.21 | 566.6 | 5.29 | 156.78 | 88.0004
977.0812 | 568.1697 | 15.6959 | 566.6043 | 145.0593 | 11.8654 | 256.8136 | 972.6942 | 125.6965 | 3.6986 | 564.6576 | 15.5759 | 566.6043 | 2.2319 | 12.0401 | 2.4822 | 17.1058 | -92.9995 | 36.8581 | 2.46 | 321.15 | 3.57 | 5.61 | 27 | 355.7 | 177.32 | 2416.9108 | 337.82 | 318.19 | 4337 | 2.27 | 566.59 | 5.37 | 157.63 | 87.7654
947.621 | 568.4794 | 15.3954 | 566.7403 | 131.3224 | 3.8228 | 255.3656 | 945.8709 | 126.4898 | 3.4266 | 565.0201 | 15.2801 | 566.7403 | 2.164 | 11.7629 | 2.4095 | 16.8007 | -93.0634 | 36.7057 | 2.39 | 321.02 | 3.2 | 4.86 | 26.5 | 354.48 | 175.49 | 2464.4631 | 328.18 | 308.83 | 4337 | 2.19 | 566.52 | 5.24 | 154.54 | 85.8959
947.3389 | 567.9961 | 15.2621 | 566.7457 | 133.2022 | 7.0152 | 255.4161 | 940.2892 | 127.3229 | 3.4739 | 564.7435 | 15.1456 | 566.7457 | 2.1627 | 11.72 | 2.4083 | 16.6905 | -92.8796 | 37.1797 | 2.4 | 321.75 | 3.06 | 5.03 | 27.5 | 360.13 | 173.71 | 2440.5723 | 328.23 | 308.69 | 4337 | 2.2 | 566.96 | 5.22 | 154.39 | 87.11
936.2324 | 567.9245 | 15.1914 | 566.4118 | 135.391 | 2.8928 | 254.8727 | 933.4814 | 128.63 | 3.5417 | 564.5645 | 15.0737 | 566.4118 | 2.1387 | 11.6116 | 2.3813 | 16.5965 | -92.959 | 37.0127 | 2.37 | 321.42 | 3.27 | 4.69 | 28.5 | 360.22 | 177.04 | 2519.3506 | 324.25 | 304.77 | 4337 | 2.17 | 566.54 | 5.18 | 155.04 | 84.2371
980.1345 | 568.3514 | 15.8522 | 566.6141 | 129.9403 | 5.4937 | 257.2233 | 975.4616 | 132.8317 | 3.539 | 564.9583 | 15.731 | 566.6141 | 2.2376 | 12.1292 | 2.4899 | 17.3476 | -92.962 | 36.8646 | 2.47 | 320.73 | 3.67 | 5.4 | 27 | 363.93 | 181.19 | 2458.3027 | 339.37 | 319.66 | 4337 | 2.27 | 566.6 | 5.43 | 156.23 | 85.8065
931.155 | 567.7204 | 15.245 | 565.7827 | 125.0609 | 4.6111 | 254.4853 | 928.678 | 129.6074 | 3.8013 | 564.4231 | 15.1286 | 565.7827 | 2.1269 | 11.5461 | 2.3692 | 16.6685 | -92.9876 | 36.8928 | 2.36 | 321.33 | 3.7 | 5.3 | 28.5 | 360.19 | 173.55 | 2484.3593 | 322.85 | 302.97 | 4337 | 2.16 | 566.29 | 5.2 | 154.31 | 85.5597
1030.6732 | 567.9683 | 16.2725 | 566.2364 | 145.2033 | 10.7528 | 259.9916 | 1022.612 | 127.0363 | 3.483 | 564.5627 | 16.1406 | 566.2364 | 2.3516 | 12.7155 | 2.6144 | 17.8036 | -92.9155 | 36.8306 | 2.59 | 321.02 | 3.12 | 5.22 | 26.5 | 362.4 | 188.53 | 2432.989 | 356.67 | 336.07 | 4337 | 2.39 | 566.58 | 5.59 | 159.07 | 86.6257
1083.1989 | 568.0533 | 16.758 | 566.0718 | 155.5637 | 10.0366 | 262.5784 | 1082.2237 | 128.8363 | 2.9449 | 564.714 | 16.608 | 566.0718 | 2.4686 | 13.4247 | 2.7439 | 18.3762 | -92.6691 | 37.3488 | 2.72 | 320.44 | 2.38 | 4.53 | 28 | 361.84 | 189.19 | 2310.0142 | 375.99 | 355.2 | 4337 | 2.51 | 566.54 | 5.85 | 160.72 | 89.9228
1076.0973 | 567.9173 | 16.9 | 566.4038 | 136.3245 | 10.8341 | 262.3328 | 1073.2768 | 127.2326 | 3.4679 | 564.552 | 16.7585 | 566.4038 | 2.4542 | 13.288 | 2.7257 | 18.5286 | -92.8047 | 36.9968 | 2.71 | 320.07 | 3.01 | 4.94 | 28.5 | 362.54 | 186.19 | 2279.0303 | 375.04 | 354.32 | 4337 | 2.51 | 566.44 | 5.89 | 160.96 | 90.842
1031.8945 | 568.2467 | 16.4208 | 566.5703 | 143.3722 | 11.8391 | 259.9189 | 1029.4592 | 126.6293 | 3.1541 | 564.8697 | 16.2889 | 566.5703 | 2.3532 | 12.7491 | 2.6173 | 17.9373 | -92.6617 | 37.4564 | 2.59 | 320.52 | 2.82 | 4.81 | 29.5 | 360.41 | 186.66 | 2410.5063 | 356.1 | 335.84 | 4337 | 2.39 | 566.56 | 5.65 | 159.3 | 87.3454
1062.3095 | 567.6497 | 16.5548 | 566.1362 | 154.5033 | 12.8959 | 261.5944 | 1054.3418 | 126.0708 | 3.2589 | 564.4187 | 16.4161 | 566.1362 | 2.4226 | 13.1071 | 2.692 | 18.1206 | -92.6703 | 37.3401 | 2.67 | 320.93 | 2.9 | 4.53 | 27.5 | 360.28 | 181.66 | 2268.3963 | 367.85 | 347.32 | 4337 | 2.47 | 566.51 | 5.73 | 160.99 | 92.3068
1041.0016 | 568.3514 | 16.3888 | 566.2687 | 129.44 | 5.2566 | 260.4227 | 1042.2635 | 125.6584 | 3.2801 | 564.9413 | 16.2535 | 566.2687 | 2.3738 | 12.9152 | 2.6392 | 17.9875 | -92.5905 | 37.5742 | 2.62 | 320.49 | 3.42 | 4.67 | 27.5 | 356.99 | 174.5 | 2224.5929 | 360.6 | 340.2 | 4337 | 2.41 | 566.59 | 5.69 | 158.98 | 93.8059
909.2365 | 568.2333 | 14.8002 | 566.172 | 124.4819 | 4.0821 | 253.4036 | 909.1535 | 122.0753 | 3.6807 | 564.9977 | 14.6915 | 566.172 | 2.0775 | 11.2951 | 2.3149 | 16.1689 | -92.9813 | 36.8154 | 2.3 | 321.8 | 4.44 | 5.3 | 28 | 352.46 | 156.03 | 2257.3805 | 314.82 | 295.31 | 4272.4286 | 2.11 | 565.88 | 5.05 | 152.87 | 94.3285
1006.5756 | 568.4919 | 15.8991 | 566.2848 | 123.1937 | 5.9223 | 258.7224 | 1009.9374 | 125.1948 | 3.4592 | 564.8536 | 15.7611 | 566.2848 | 2.2961 | 12.53 | 2.5551 | 17.4562 | -92.7977 | 36.8798 | 2.53 | 320.91 | 4 | 4.96 | 29 | 356.14 | 169.59 | 2209.4995 | 348.22 | 327.93 | 4272.4286 | 2.33 | 566.48 | 5.5 | 157.63 | 94.9882
1096.0474 | 568.0309 | 16.6611 | 566.0744 | 121.2233 | 9.7098 | 262.6026 | 1089.232 | 127.3153 | 3.2622 | 564.5439 | 16.5021 | 566.0744 | 2.4972 | 13.5367 | 2.7741 | 18.3817 | -92.5424 | 36.9593 | 2.73 | 321.73 | 3.38 | 4.76 | 27 | 360.58 | 189.1 | 2306.6186 | 377.18 | 350.26 | 4272.4286 | 2.52 | 566.56 | 5.96 | 160.35 | 92.5602
1430.4664 | 567.7177 | 19.7361 | 566.5926 | 142.7099 | 16.3226 | 277.404 | 1404.4443 | 134.9625 | 2.8293 | 563.9533 | 19.4957 | 566.5926 | 3.2514 | 17.3505 | 3.5986 | 22.0354 | -92.8293 | 36.3213 | 3.56 | 322.77 | 2.68 | 4.12 | 28.5 | 377.84 | 250.13 | 2330.4749 | 496.55 | 458.56 | 4272.4286 | 2.31 | 566.59 | 7.35 | 172.6 | 89.199
1426.8117 | 568.0309 | 19.8169 | 566.0654 | 132.5731 | 15.635 | 277.2517 | 1401.519 | 133.2491 | 2.7904 | 564.1654 | 19.5797 | 566.0654 | 3.2432 | 17.3185 | 3.5896 | 22.0978 | -92.7721 | 36.6998 | 3.55 | 322.35 | 2.91 | 4.04 | 26.5 | 375.12 | 259.93 | 2427.234 | 495.08 | 457.53 | 4272.4286 | 3.3 | 566.44 | 7.37 | 171.77 | 85.2698
1341.3944 | 568.6002 | 18.9853 | 566.5461 | 114.5198 | 19.4683 | 274.04 | 1324.7547 | 129.6257 | 3.139 | 564.6835 | 18.7657 | 566.5461 | 3.0496 | 16.3833 | 3.3791 | 21.1495 | -93.0413 | 36.3163 | 3.35 | 322.29 | 3.28 | 4.27 | 27 | 372.8 | 246.07 | 2412.4383 | 467.53 | 435.79 | 4272.4286 | 3.11 | 566.62 | 6.95 | 170 | 85.2706
1344.4167 | 567.8385 | 19.1198 | 566.1049 | 113.4572 | 8.7869 | 274.8393 | 1353.9588 | 130.9181 | 2.7479 | 563.9318 | 18.8907 | 566.1049 | 3.0567 | 16.7098 | 3.3872 | 21.3442 | -92.9145 | 36.38 | 3.33 | 320.53 | 3.15 | 4.27 | 27.5 | 368.38 | 244.4 | 2376.2182 | 466.35 | 439.43 | 4272.4286 | 3.09 | 566.46 | 6.86 | 168.92 | 84.9293
1236.0269 | 567.4322 | 18.0103 | 565.1822 | 118.8069 | 17.7165 | 269.4699 | 1238.5187 | 128.9616 | 3.1027 | 563.6052 | 17.8104 | 565.1822 | 2.8147 | 15.2822 | 3.1201 | 20.0023 | -92.7548 | 36.5895 | 3.09 | 320.9 | 3.29 | 4.75 | 28 | 368.62 | 224.05 | 2369.1655 | 429.53 | 404.04 | 4272.4286 | 2.86 | 565.79 | 6.41 | 165.78 | 86.5204
1258.4631 | 567.7938 | 18.3011 | 566.0189 | 124.3008 | 15.4929 | 270.9801 | 1263.5352 | 131.052 | 3.0443 | 563.9282 | 18.094 | 566.0189 | 2.8637 | 15.5838 | 3.1757 | 20.3106 | -92.8101 | 36.5202 | 3.15 | 320.47 | 3.42 | 4.64 | 27.5 | 367.61 | 230.69 | 2381.4975 | 439.49 | 413.86 | 4272.4286 | 2.92 | 566.06 | 6.53 | 167.11 | 85.1611
1396.1581 | 567.9119 | 19.4445 | 566.4754 | 92.554 | 18.1162 | 276.0256 | 1383.5784 | 134.558 | 2.6811 | 563.9595 | 19.2077 | 566.4754 | 3.1733 | 17.0676 | 3.5139 | 21.763 | -92.5722 | 37.2659 | 3.45 | 321.75 | 2.55 | 4.1 | 27 | 373.66 | 244.54 | 2331.5771 | 479.73 | 448.1 | 4272.4286 | 3.21 | 566.2 | 7.14 | 170.97 | 88.6747
1197.9214 | 568.0918 | 17.7531 | 565.3317 | 90.887 | 13.7855 | 267.4502 | 1193.1285 | 130.6506 | 2.9718 | 564.2495 | 17.5675 | 565.3317 | 2.7273 | 14.7383 | 3.0259 | 19.7311 | -92.8676 | 36.7123 | 3.02 | 321.04 | 2.56 | 3.96 | 27.5 | 368.38 | 207.27 | 2250.1493 | 417.97 | 393.55 | 4272.4286 | 2.8 | 565.06 | 6.35 | 164.33 | 91.2951
1108.5457 | 568.4149 | 17.3561 | 566.2561 | 103.9803 | 6.8139 | 263.886 | 1115.2517 | 126.6468 | 3.3297 | 564.748 | 17.1964 | 566.2561 | 2.5263 | 13.7413 | 2.8055 | 19.136 | -92.9891 | 36.3027 | 2.8 | 319.48 | 2.9 | 4.18 | 27.5 | 360.2 | 192.63 | 2252.0124 | 388.79 | 365.45 | 4272.4286 | 2.58 | 565.54 | 6.11 | 159.57 | 91.1358
1109.054 | 568.3031 | 17.0317 | 565.2923 | 86.1929 | 7.4784 | 263.3789 | 1119.7051 | 127.2942 | 3.5582 | 564.6594 | 16.8646 | 565.2923 | 2.5265 | 13.7898 | 2.8075 | 18.9014 | -93.0442 | 36.1489 | 2.77 | 320.23 | 3.44 | 4.4 | 27.5 | 364.68 | 191.76 | 2263.6446 | 385.81 | 361.93 | 4272.4286 | 2.56 | 564.69 | 6 | 157.14 | 91.3788
1042.9297 | 567.8054 | 16.3579 | 565.0989 | 84.1913 | 6.0493 | 260.294 | 1048.0571 | 125.6494 | 3.8583 | 564.3873 | 16.2115 | 565.0989 | 2.3772 | 12.9324 | 2.6436 | 18.0825 | -92.9547 | 36.8726 | 2.63 | 321.01 | 4.21 | 5.34 | 28 | 365.62 | 190.77 | 2390.9507 | 362.5 | 340.89 | 4272.4286 | 2.42 | 564.88 | 5.7 | 156.75 | 86.954
1045.0251 | 567.3124 | 16.0815 | 566.2642 | 112.8337 | 7.573 | 260.3039 | 1048.2509 | 126.2978 | 3.785 | 563.8486 | 15.9315 | 566.2642 | 2.3816 | 12.9593 | 2.6484 | 17.7917 | -92.9457 | 36.7259 | 2.64 | 321.88 | 4.03 | 5.17 | 25.5 | 365.63 | 197.45 | 2470.1072 | 363.94 | 341.52 | 4272.4286 | 2.43 | 565.34 | 5.62 | 158.18 | 84.3727
1002.6451 | 567.7974 | 15.6668 | 565.2788 | 110.0904 | 10.7666 | 258.2576 | 1002.6854 | 124.402 | 3.7936 | 564.3793 | 15.5262 | 565.2788 | 2.2888 | 12.3983 | 2.5452 | 17.251 | -92.8741 | 37.0981 | 2.51 | 322.13 | 4.1 | 5.21 | 27.5 | 361.3 | 185.25 | 2449.0745 | 344.74 | 323.17 | 4272.4286 | 2.31 | 565.33 | 5.38 | 155.68 | 86.8287
993.7363 | 567.1816 | 15.8397 | 564.8205 | 105.302 | 6.8049 | 257.9812 | 998.3445 | 123.9063 | 3.7101 | 563.8235 | 15.7059 | 564.8205 | 2.2676 | 12.307 | 2.5231 | 17.4185 | -92.9597 | 36.8827 | 2.5 | 321.28 | 4.11 | 4.99 | 27.5 | 361.14 | 175.45 | 2324.4778 | 343.6 | 322.48 | 4272.4286 | 2.3 | 564.86 | 5.45 | 153.97 | 90.6059
918.3994 | 568.6047 | 14.8607 | 565.3335 | 101.8021 | 3.5606 | 254.1221 | 920.2752 | 121.7047 | 3.7605 | 565.1257 | 14.7447 | 565.3335 | 2.0976 | 11.3915 | 2.338 | 16.3465 | -93.2967 | 35.9761 | 2.33 | 322.28 | 4.05 | 5.09 | 27 | 356.89 | 160.75 | 2293.7442 | 320.07 | 299.42 | 4272.4286 | 2.14 | 564.49 | 5.12 | 150.09 | 92.2537
932.6522 | 568.167 | 14.8599 | 565.7353 | 108.5311 | 4.5285 | 254.8841 | 933.6887 | 121.4512 | 3.6297 | 564.7677 | 14.7386 | 565.7353 | 2.1294 | 11.5683 | 2.3726 | 16.3543 | -93.0282 | 36.6941 | 2.36 | 322.56 | 3.38 | 4.45 | 27.5 | 355.11 | 162.77 | 2293.9904 | 323.58 | 303.15 | 4272.4286 | 2.16 | 565.18 | 5.11 | 150.99 | 92.4776
1065.4743 | 568.1017 | 16.5907 | 565.6547 | 108.9167 | 7.1103 | 261.6714 | 1073.4874 | 125.8962 | 3.7937 | 564.6316 | 16.4417 | 565.6547 | 2.4294 | 13.2254 | 2.6999 | 18.3254 | -92.849 | 36.8126 | 2.66 | 320.9 | 3.58 | 4.63 | 27 | 361.42 | 189.29 | 2342.6453 | 367.69 | 345.22 | 4272.4286 | 2.45 | 565.18 | 5.75 | 156.45 | 89.3586
1017.8711 | 568.0032 | 16.0271 | 564.0859 | 84.635 | 4.5425 | 258.9726 | 1022.1182 | 123.1877 | 3.8691 | 564.4267 | 15.8867 | 564.0859 | 2.3228 | 12.6286 | 2.5836 | 17.7481 | -93.1394 | 36.3359 | 2.54 | 321.22 | 4.06 | 5.17 | 27 | 360.01 | 182.64 | 2377.4911 | 350.43 | 328.21 | 4272.4286 | 2.34 | 564.42 | 5.55 | 148.39 | 89.014
1001.4982 | 567.7965 | 15.942 | 564.7857 | 87.8313 | 6.0783 | 258.6625 | 1026.0955 | 124.2638 | 3.5975 | 564.4822 | 15.7991 | 564.7857 | 2.2844 | 12.6379 | 2.5416 | 17.6438 | -93.1173 | 36.4232 | 2.53 | 319.1 | 4.14 | 5.28 | 26 | 359.01 | 176.47 | 2299.5561 | 350.51 | 327.87 | 4272.4286 | 2.32 | 564.45 | 5.56 | 155.18 | 90.0607
1065.837 | 568.0158 | 16.7365 | 565.5732 | 115.2202 | 6.8133 | 261.1899 | 1076.4724 | 124.6863 | 3.7008 | 564.5404 | 16.5867 | 565.5732 | 2.4277 | 13.2423 | 2.7003 | 18.4606 | -92.8275 | 37.038 | 2.66 | 320.37 | 3.92 | 5.06 | 28 | 362.21 | 192.62 | 2396.7009 | 366.14 | 343.37 | 4272.4286 | 2.45 | 565.42 | 5.8 | 153.6 | 87.7542
928.4241 | 568.4821 | 15.1121 | 566.1496 | 118.7518 | 5.06 | 255.0991 | 940.827 | 122.487 | 3.8813 | 565.0093 | 14.9928 | 566.1496 | 2.1208 | 11.6252 | 2.3631 | 16.5811 | -93.0405 | 36.7302 | 2.35 | 320.79 | 3.89 | 4.87 | 27.5 | 355.83 | 174.57 | 2461.5923 | 323.55 | 302.99 | 4272.4286 | 2.16 | 565.77 | 5.18 | 154.29 | 85.4236
893.5393 | 568.4624 | 14.5823 | 564.7205 | 105.4508 | 1.8844 | 252.5733 | 890.68 | 121.2068 | 3.93 | 565.0228 | 14.4741 | 564.7205 | 2.042 | 11.0331 | 2.2757 | 15.9957 | -93.1883 | 36.403 | 2.27 | 322.88 | 4.23 | 5.3 | 27 | 357.43 | 165.98 | 2446.8211 | 309.12 | 289.82 | 4272.4286 | 2.07 | 564.42 | 4.98 | 147.88 | 87.2786
869.175 | 568.2646 | 14.0527 | 564.9316 | 105.8568 | 2.7497 | 251.111 | 859.3958 | 123.3624 | 3.7515 | 564.8804 | 13.9463 | 564.9316 | 1.9865 | 10.6781 | 2.2154 | 15.4026 | -93.3694 | 35.8085 | 2.2 | 324.44 | 4.43 | 5.4 | 27.5 | 359.27 | 155.51 | 2366.706 | 299.83 | 280.73 | 4272.4286 | 2.02 | 564.69 | 4.77 | 147.03 | 91.1027
877.6963 | 567.2712 | 14.1459 | 565.3021 | 106.7589 | 3.4595 | 251.786 | 876.5556 | 121.9085 | 4.0524 | 563.9506 | 14.0404 | 565.3021 | 2.0059 | 10.8621 | 2.2368 | 15.5455 | -93.1784 | 36.3149 | 2.22 | 323.73 | 4.57 | 5.49 | 25 | 357.95 | 157.86 | 2384.1266 | 302.12 | 282.89 | 4272.4286 | 2.03 | 564.58 | 4.79 | 150.17 | 90.1826
871.6053 | 568.5501 | 14.3334 | 565.5107 | 111.9383 | 1.6694 | 251.4692 | 869.7601 | 122.4255 | 4.1814 | 564.9807 | 14.2306 | 565.5107 | 1.9934 | 10.7903 | 2.2224 | 15.7034 | -93.2293 | 36.1061 | 2.21 | 322.91 | 4.83 | 5.86 | 25 | 357.39 | 164.47 | 2491.7955 | 301.2 | 282 | 4272.4286 | 2.02 | 565.04 | 4.88 | 147.88 | 86.0934
870.3623 | 568.2368 | 14.2283 | 565.2448 | 118.7072 | 2.4511 | 251.357 | 868.9895 | 123.0103 | 3.9633 | 564.8464 | 14.1248 | 565.2448 | 1.9902 | 10.7653 | 2.2189 | 15.5712 | -93.4877 | 35.5629 | 2.21 | 323.18 | 4.48 | 5.56 | 26 | 358.15 | 163.59 | 2477.848 | 301.04 | 282.07 | 4272.4286 | 2.02 | 564.87 | 4.83 | 140.51 | 86.4556
881.2301 | 568.0193 | 14.3319 | 565.3065 | 116.0299 | 2.3715 | 252.0939 | 878.7349 | 125.4684 | 3.8192 | 564.5037 | 14.2242 | 565.3065 | 2.0148 | 10.9149 | 2.2458 | 15.7117 | -93.4089 | 35.7399 | 2.24 | 323.26 | 4.36 | 5.66 | 26.5 | 358.27 | 159.43 | 2365.9371 | 306.91 | 287.9 | 4272.4286 | 2.05 | 565.51 | 5.73 | 160.99 | 90.2066
954.2948 | 568.2637 | 15.2699 | 566.2105 | 118.8298 | 5.1911 | 255.9846 | 950.8042 | 125.7111 | 3.5551 | 564.7865 | 15.1563 | 566.2105 | 2.1794 | 11.7605 | 2.4256 | 16.747 | -92.954 | 36.7584 | 2.41 | 322.65 | 3.92 | 5.64 | 27 | 359.82 | 174.5 | 2191.472 | 360.6 | 340.2 | 4272.4286 | 2.41 | 566.59 | 5.69 | 158.98 | 88.1746
912.1937 | 568.3156 | 14.8643 | 565.6377 | 106.6357 | 2.3047 | 253.6784 | 919.0886 | 123.4764 | 3.6504 | 564.8894 | 14.7571 | 565.6377 | 2.0835 | 11.328 | 2.3221 | 16.3308 | -93.0117 | 36.7512 | 2.3 | 322.53 | 4.21 | 5.67 | 28 | 357.13 | 158.73 | 2291.0248 | 314.92 | 295.66 | 4267.4 | 2.11 | 565.75 | 5.07 | 152.07 | 92.7338
918.1607 | 568.1268 | 14.7123 | 565.4212 | 109.2773 | 3.6639 | 254.1121 | 918.5692 | 122.5318 | 3.8054 | 564.5923 | 14.6014 | 565.4212 | 2.097 | 11.3916 | 2.336 | 16.1821 | -93.022 | 36.7172 | 2.32 | 322.9 | 4.32 | 5.7 | 27.5 | 357.96 | 164.77 | 2356.9185 | 317.86 | 298.33 | 4267.4 | 2.13 | 565.59 | 5.04 | 151.5 | 90.0954
949.8807 | 568.3926 | 15.5086 | 565.9313 | 121.5745 | 3.8194 | 255.7777 | 950.5395 | 123.7785 | 3.672 | 564.893 | 15.3961 | 565.9313 | 2.1697 | 11.7351 | 2.4156 | 16.9542 | -93.1355 | 36.4354 | 2.39 | 321.59 | 3.86 | 5.29 | 28 | 358.6 | 174.83 | 2430.9066 | 326.53 | 306.91 | 4267.4 | 2.19 | 565.57 | 5.26 | 152.97 | 87.5613
917.0944 | 568.2306 | 14.8215 | 565.4686 | 128.9264 | 3.332 | 253.8391 | 914.8672 | 122.9859 | 3.7074 | 564.8769 | 14.7096 | 565.4686 | 2.0954 | 11.3467 | 2.3343 | 16.2251 | -93.0963 | 36.6059 | 2.32 | 322.69 | 3.85 | 5.14 | 28 | 358.39 | 167.94 | 2406.0537 | 317.2 | 297.86 | 4267.4 | 2.13 | 565.36 | 5.07 | 152.41 | 88.4649
899.2769 | 568.2941 | 14.6347 | 565.201 | 125.511 | 2.0508 | 253.0313 | 896.0217 | 125.0995 | 3.6517 | 564.9225 | 14.5244 | 565.201 | 2.0562 | 11.131 | 2.2913 | 16.0132 | -93.0672 | 36.5092 | 2.28 | 322.89 | 4.06 | 5.19 | 27.5 | 357.95 | 161.59 | 2360.8914 | 311.2 | 292.08 | 4267.4 | 2.09 | 565.11 | 4.98 | 145.96 | 90.3078
948.9725 | 567.8565 | 15.3002 | 565.6019 | 110.6227 | 1.9104 | 255.7777 | 943.8342 | 126.0955 | 3.5162 | 564.3014 | 15.1841 | 565.6019 | 2.1678 | 11.6767 | 2.4142 | 16.7815 | -93.201 | 36.2852 | 2.4 | 322.62 | 3.94 | 4.98 | 27.5 | 359.88 | 160.28 | 2243.3628 | 328.45 | 304.89 | 4267.4 | 2.2 | 565.62 | 5.47 | 150.36 | 95.4881
993.0233 | 567.1484 | 15.7735 | 564.5691 | 104.4982 | 3.8521 | 257.683 | 974.0866 | 126.0874 | 3.4501 | 563.8718 | 15.6511 | 564.5691 | 2.2659 | 12.0768 | 2.5207 | 17.3123 | -93.0997 | 36.4486 | 2.5 | 323.43 | 3.44 | 4.81 | 28 | 363.9 | 165.98 | 2246.9405 | 341.83 | 315.23 | 4267.4 | 2.3 | 565.52 | 5.81 | 155.01 | 96.5756
897.4667 | 567.7088 | 14.4 | 564.9674 | 110.5651 | 1.5531 | 252.5644 | 875.701 | 124.4365 | 3.8691 | 564.3999 | 14.292 | 564.9674 | 2.0515 | 10.8806 | 2.2861 | 15.77 | -93.2606 | 36.4608 | 2.27 | 325.43 | 4.33 | 6.05 | 28 | 362.88 | 159.83 | 2416.8475 | 307.05 | 282.21 | 4267.4 | 2.08 | 564.98 | 5.34 | 149.53 | 91.7269
914.1001 | 568.005 | 14.5997 | 566.5578 | 118.5612 | 4.9855 | 253.3246 | 891.0448 | 124.2188 | 3.7518 | 564.6209 | 14.497 | 566.5578 | 2.0887 | 11.0432 | 2.3267 | 15.9593 | -93.2044 | 36.6319 | 2.32 | 325.69 | 4.35 | 6.24 | 28.5 | 360.77 | 162.74 | 2405.6972 | 313.64 | 288.68 | 4267.4 | 2.12 | 565.89 | 5.4 | 152.98 | 91.7511
995.2924 | 568.2816 | 15.7271 | 566.0396 | 116.0078 | 2.3408 | 257.878 | 976.8056 | 126.1246 | 3.4223 | 564.6656 | 15.6109 | 566.0396 | 2.2712 | 12.0937 | 2.5273 | 17.2545 | -93.0836 | 36.801 | 2.52 | 324.02 | 3.83 | 5.46 | 28 | 364.24 | 167.25 | 2249.4332 | 343.14 | 317.29 | 4267.4 | 2.31 | 566.09 | 5.8 | 156.52 | 96.1573
1019.6194 | 568.3881 | 16.0175 | 566.0387 | 88.2568 | 3.7562 | 259.0619 | 1005.1775 | 126.1157 | 3.6624 | 564.9404 | 15.8903 | 566.0387 | 2.3244 | 12.4416 | 2.5868 | 17.6884 | -93.1506 | 36.5742 | 2.57 | 323.24 | 3.84 | 5.61 | 27.5 | 364.87 | 168.69 | 2217.5021 | 351.53 | 324.63 | 4267.4 | 2.36 | 566 | 5.95 | 156.24 | 97.2551
1034.6564 | 567.8743 | 16.1277 | 565.6135 | 105.181 | 4.1169 | 260.2246 | 1023.5564 | 126.2454 | 3.5446 | 564.4124 | 15.9928 | 565.6135 | 2.3598 | 12.6826 | 2.6241 | 17.7981 | -92.8349 | 37.442 | 2.6 | 322.72 | 3.83 | 5.33 | 29 | 362.02 | 178.48 | 2299.9322 | 356.4 | 331.16 | 4267.4 | 2.4 | 566.08 | 5.9 | 158.57 | 92.9463
981.8487 | 568.3245 | 16.0366 | 565.7236 | 106.2732 | 4.486 | 257.7022 | 985.6705 | 125.0285 | 3.592 | 564.8867 | 15.9133 | 565.7236 | 2.2404 | 12.1711 | 2.4935 | 17.5931 | -93.1003 | 36.8509 | 2.47 | 321.04 | 3.78 | 5.1 | 29 | 358.89 | 177.18 | 2368.1343 | 339.28 | 319.28 | 4267.4 | 2.27 | 566.01 | 5.52 | 153.77 | 88.8454
974.5022 | 568.0623 | 15.8159 | 565.107 | 112.6935 | 3.7487 | 257.5096 | 975.4614 | 125.8996 | 3.777 | 564.6952 | 15.6934 | 565.107 | 2.2236 | 12.0999 | 2.4758 | 17.3652 | -93.0317 | 36.9845 | 2.46 | 321.36 | 4.22 | 5.12 | 27.5 | 361.56 | 187.55 | 2519.9171 | 337.65 | 317.61 | 4267.4 | 2.26 | 565.89 | 5.45 | 148.67 | 83.4269
933.4643 | 568.7721 | 15.3538 | 566.2767 | 119.5657 | 2.3564 | 255.3613 | 934.3754 | 126.0381 | 3.6255 | 565.1901 | 15.2393 | 566.2767 | 2.1313 | 11.5855 | 2.3746 | 16.779 | -93.0691 | 36.8964 | 2.36 | 321.71 | 4.04 | 5.22 | 27.5 | 361.23 | 185.2 | 2603.1702 | 323.27 | 303.6 | 4267.4 | 2.17 | 566.12 | 5.27 | 152.05 | 81.2708
877.5909 | 568.3174 | 14.2293 | 566.2687 | 115.2025 | 1.4488 | 252.0633 | 874.3308 | 123.0598 | 3.6615 | 564.7721 | 14.1234 | 566.2687 | 2.0065 | 10.8785 | 2.2379 | 15.5838 | -93.1917 | 36.6985 | 2.23 | 323.81 | 4.13 | 5.65 | 31 | 358.87 | 172.61 | 2587.6341 | 303.76 | 284.66 | 4267.4 | 2.04 | 565.87 | 4.84 | 148.95 | 82.7052
886.2796 | 568.9037 | 14.3974 | 566.4092 | 106.1348 | 3.1453 | 252.6454 | 885.6318 | 123.3867 | 3.5405 | 565.3226 | 14.2881 | 566.4092 | 2.0259 | 10.9883 | 2.2588 | 15.8055 | -93.1078 | 36.9607 | 2.25 | 323.7 | 4.11 | 5.41 | 28 | 358.63 | 170.84 | 2541.6351 | 305.69 | 286.84 | 4267.4 | 2.06 | 566.03 | 4.91 | 148.16 | 84.2139
908.5484 | 567.9603 | 14.838 | 565.9017 | 102.8946 | 2.6491 | 254.0362 | 907.1636 | 124.9514 | 3.686 | 564.5475 | 14.7265 | 565.9017 | 2.0746 | 11.2682 | 2.3126 | 16.3172 | -93.1665 | 36.71 | 2.3 | 322.5 | 4.18 | 5.37 | 27 | 359.96 | 178.17 | 2575.706 | 314.27 | 295.19 | 4267.4 | 2.11 | 565.78 | 5.08 | 152.2 | 82.5088
884.2771 | 568.5367 | 14.5888 | 565.9384 | 100.3153 | 2.206 | 252.6663 | 883.2934 | 124.0606 | 3.8576 | 564.9834 | 14.4824 | 565.9384 | 2.021 | 10.971 | 2.2539 | 16.0169 | -93.3427 | 36.2441 | 2.25 | 322.77 | 4.37 | 5.65 | 26.5 | 360.03 | 174.95 | 2590.2287 | 307.27 | 288.23 | 4267.4 | 2.06 | 566.07 | 4.99 | 149.21 | 82.0539
870.6412 | 568.3899 | 14.0912 | 566.4145 | 103.5861 | 2.277 | 251.9581 | 868.2258 | 126.1522 | 3.7524 | 564.9744 | 13.9791 | 566.4145 | 1.9915 | 10.8121 | 2.2203 | 15.4996 | -93.2487 | 36.5049 | 2.21 | 324.04 | 4.31 | 5.58 | 27.5 | 360.64 | 170.36 | 2581.1058 | 300.62 | 281.66 | 4267.4 | 2.02 | 566.34 | 4.8 | 150.85 | 83.209
888.5424 | 568.0659 | 14.5188 | 565.661 | 116.18 | 7.2616 | 252.9189 | 884.9759 | 126.0737 | 3.9124 | 564.7596 | 14.4088 | 565.661 | 2.032 | 10.9914 | 2.2644 | 15.9095 | -93.1213 | 36.8617 | 2.25 | 323.26 | 4.33 | 5.42 | 27 | 360.03 | 172.68 | 2572.2376 | 305.23 | 286.48 | 4267.4 | 2.05 | 565.61 | 4.92 | 148.82 | 83.5671
880.1079 | 568.5161 | 14.4425 | 566.5622 | 119.4348 | 4.8075 | 252.3762 | 878.9174 | 124.6167 | 3.8016 | 565.0496 | 14.3341 | 566.5622 | 2.0124 | 10.9187 | 2.2433 | 15.8028 | -93.2675 | 36.4174 | 2.22 | 323.36 | 4.21 | 5.25 | 26.5 | 359.16 | 173.39 | 2601.7035 | 303.09 | 284.4 | 4267.4 | 2.03 | 566.24 | 4.88 | 144.76 | 82.474
863.1336 | 568.3228 | 14.0778 | 566.1397 | 119.3898 | 1.6713 | 251.4034 | 865.8385 | 124.5746 | 3.9428 | 564.9198 | 13.9737 | 566.1397 | 1.9736 | 10.7614 | 2.2018 | 15.428 | -93.1273 | 36.8776 | 2.2 | 323.72 | 4.34 | 5.25 | 26 | 359.13 | 174.08 | 2651.4937 | 298.63 | 280.17 | 4267.4 | 2.01 | 566.32 | 4.79 | 148.46 | 80.6255
908.1175 | 567.8985 | 14.8722 | 565.6592 | 98.5371 | 2.624 | 253.9888 | 909.804 | 127.7927 | 3.7421 | 564.4124 | 14.7609 | 565.6592 | 2.0748 | 11.2823 | 2.3119 | 16.3455 | -93.0642 | 36.9629 | 2.3 | 322.19 | 4 | 5.24 | 28 | 360.76 | 177.57 | 2576.2833 | 313.07 | 294.13 | 4267.4 | 2.1 | 565.7 | 5.1 | 150.65 | 82.6876
897.9595 | 568.7354 | 14.7231 | 566.4566 | 103.9918 | 5.6875 | 253.2893 | 896.5817 | 125.7715 | 3.6404 | 565.1892 | 14.6173 | 566.4566 | 2.0523 | 11.1153 | 2.2873 | 16.1768 | -93.0215 | 37.1297 | 2.27 | 323.09 | 3.85 | 5.01 | 25.5 | 361.84 | 173.97 | 2561.5001 | 308.52 | 289.83 | 4267.4 | 2.08 | 566.33 | 5.01 | 151.99 | 83.7816
908.7406 | 567.4304 | 14.7192 | 566.0172 | 122.8944 | 4.1467 | 253.8537 | 906.2117 | 125.3007 | 3.6062 | 563.7796 | 14.6046 | 566.0172 | 2.0776 | 11.2541 | 2.3137 | 16.1213 | -93.0472 | 36.9968 | 2.3 | 322.74 | 3.96 | 4.56 | 28.5 | 356.41 | 177.41 | 2573.8745 | 312.96 | 294.14 | 4267.4 | 2.11 | 566.41 | 5.01 | 153.25 | 83.0595
916.5737 | 567.8887 | 14.8901 | 565.9134 | 106.9976 | 4.8285 | 254.2242 | 913.1766 | 124.3568 | 3.7551 | 564.3354 | 14.7781 | 565.9134 | 2.0949 | 11.3198 | 2.3334 | 16.3541 | -93.1543 | 36.6226 | 2.32 | 322.54 | 3.84 | 5.25 | 27.5 | 359.17 | 177.08 | 2548.5521 | 315.63 | 296.51 | 4267.4 | 2.12 | 566.22 | 5.08 | 153.64 | 83.9006
964.3381 | 567.9442 | 15.5612 | 566.1962 | 99.0118 | 4.0686 | 256.7302 | 961.6114 | 126.7036 | 3.6637 | 564.6701 | 15.4393 | 566.1962 | 2.2021 | 11.9101 | 2.451 | 17.1198 | -92.9378 | 36.9615 | 2.43 | 322.28 | 3.68 | 5.87 | 28 | 361.96 | 191.22 | 2608.568 | 332.46 | 312.82 | 4267.4 | 2.23 | 566.69 | 5.36 | 155.48 | 81.2575
901.8218 | 568.7211 | 14.6815 | 565.8516 | 106.8507 | 1.9197 | 253.2031 | 901.2682 | 126.2738 | 3.6176 | 565.1964 | 14.5664 | 565.8516 | 2.0611 | 11.1725 | 2.2969 | 16.1456 | -92.9681 | 36.7347 | 2.29 | 323.25 | 3.47 | 5.43 | 29 | 359.68 | 177.35 | 2548.897 | 311.78 | 292.61 | 4205.4286 | 2.1 | 565.95 | 5.04 | 150.09 | 83.6834
900.7803 | 568.1661 | 14.6611 | 566.1085 | 112.3968 | 2.6916 | 253.1735 | 899.9614 | 126.002 | 3.6264 | 564.731 | 14.5515 | 566.1085 | 2.0594 | 11.1543 | 2.2939 | 16.0903 | -92.9099 | 36.9426 | 2.28 | 323.23 | 3.93 | 5.34 | 29 | 357.21 | 174.8 | 2530.3212 | 309.85 | 290.52 | 4205.4286 | 2.09 | 565.89 | 4.98 | 151.36 | 84.7667
940.8858 | 568.4496 | 15.0655 | 566.6177 | 103.672 | 4.1959 | 255.5168 | 936.6152 | 127.5539 | 3.6973 | 564.9859 | 14.9435 | 566.6177 | 2.1507 | 11.6307 | 2.3928 | 16.5742 | -92.8563 | 36.9886 | 2.37 | 323.48 | 4.11 | 5.25 | 28.5 | 361.34 | 189.68 | 2626.9906 | 323.19 | 303.65 | 4205.4286 | 2.17 | 566.79 | 5.15 | 153.28 | 81.3643
954.6947 | 568.4498 | 15.5381 | 566.3035 | 106.9306 | 4.0326 | 256.2957 | 952.7656 | 129.4137 | 3.7841 | 564.9324 | 15.4199 | 566.3035 | 2.1799 | 11.8035 | 2.4271 | 17.0719 | -92.9329 | 36.6342 | 2.42 | 322.01 | 3.97 | 5.92 | 28 | 364.82 | 188.81 | 2560.1385 | 329.93 | 310.15 | 4205.4286 | 2.22 | 566.31 | 5.36 | 155.53 | 82.6654
955.5719 | 568.5653 | 15.4929 | 567.2478 | 99.1944 | 3.8855 | 256.3656 | 954.7613 | 128.9733 | 3.6119 | 565.0729 | 15.3707 | 567.2478 | 2.1815 | 11.8172 | 2.4288 | 17.0399 | -92.7342 | 37.2649 | 2.42 | 322.23 | 3.88 | 5.66 | 28 | 365.02 | 186.17 | 2526.2968 | 329.46 | 309.91 | 4205.4286 | 2.22 | 566.88 | 5.37 | 155.61 | 83.9211
976.3218 | 568.7935 | 15.4613 | 567.1941 | 97.9847 | 7.0519 | 257.2684 | 974.2198 | 128.8211 | 3.4164 | 565.2474 | 15.3276 | 567.1941 | 2.2287 | 12.0714 | 2.4801 | 17.0724 | -92.8568 | 37.1623 | 2.45 | 323.17 | 3.77 | 5.22 | 28 | 367.66 | 192.17 | 2564.4387 | 334.83 | 315.14 | 4205.4286 | 2.25 | 567.23 | 5.33 | 155.9 | 83.0726
1050.2483 | 568.3827 | 16.4182 | 566.9471 | 103.9572 | 11.3618 | 261.2098 | 1043.8051 | 131.0168 | 3.581 | 564.8688 | 16.2737 | 566.9471 | 2.3957 | 12.9191 | 2.6627 | 18.1245 | -92.6347 | 37.124 | 2.65 | 322.06 | 3.88 | 4.39 | 29 | 374.52 | 206.41 | 2540.29 | 362.55 | 341.71 | 4205.4286 | 2.44 | 566.98 | 5.74 | 159.76 | 82.7651
1026.2839 | 568.0739 | 16.099 | 565.7254 | 103.7843 | 7.9941 | 260.1422 | 1026.8373 | 129.5863 | 3.5692 | 564.4392 | 15.9546 | 565.7254 | 2.3413 | 12.7132 | 2.6029 | 17.7831 | -92.6891 | 36.494 | 2.58 | 321.78 | 3.9 | 3.57 | 27 | 371.75 | 199.06 | 2507.5863 | 354.37 | 333.84 | 4205.4286 | 2.38 | 566.45 | 5.62 | 157.55 | 83.7371
951.9421 | 568.3809 | 15.3559 | 566.4861 | 112.2148 | 7.0721 | 256.0966 | 953.9985 | 126.9909 | 3.4463 | 564.7677 | 15.2332 | 566.4861 | 2.1748 | 11.7915 | 2.4202 | 16.8705 | -93.1087 | 36.8206 | 2.41 | 322.21 | 3.71 | 3.4 | 25.5 | 365.13 | 189.11 | 2570.7545 | 329.12 | 309.36 | 4205.4286 | 2.21 | 566.76 | 5.28 | 154.01 | 82.3951
1080.2417 | 568.0131 | 16.6053 | 566.0601 | 116.1818 | 6.8157 | 262.7612 | 1085.7416 | 131.1872 | 3.2591 | 564.2477 | 16.4458 | 566.0601 | 2.4637 | 13.4067 | 2.7363 | 18.3894 | -92.8291 | 37.4 | 2.71 | 321.28 | 3.71 | 3.51 | 29 | 370.17 | 211.55 | 2518.7091 | 373.97 | 353.22 | 4205.4286 | 2.5 | 566.71 | 5.86 | 160.54 | 82.2984
1091.8534 | 567.9764 | 16.8887 | 566.1765 | 107.1295 | 12.5275 | 263.3143 | 1088.5547 | 130.8516 | 3.2323 | 564.254 | 16.7277 | 566.1765 | 2.4896 | 13.4516 | 2.7655 | 18.646 | -92.9207 | 37.0518 | 2.75 | 321.07 | 3.42 | 4.3 | 27 | 369.32 | 213.75 | 2505.883 | 379.5 | 358.72 | 4205.4286 | 2.54 | 566.3 | 5.93 | 161.9 | 82.5248
1107.8854 | 567.7813 | 17.1126 | 566.2096 | 103.4892 | 8.4373 | 264.067 | 1111.2113 | 129.316 | 3.5214 | 564.2209 | 16.9495 | 566.2096 | 2.526 | 13.7019 | 2.8042 | 18.9103 | -92.6279 | 37.6053 | 2.77 | 321.1 | 3.78 | 4.39 | 27.5 | 366.4 | 216.38 | 2520.9038 | 382.02 | 360.97 | 4205.4286 | 2.56 | 566.34 | 5.98 | 160.88 | 82.3271
1146.7659 | 567.6622 | 17.394 | 566.0189 | 97.4889 | 11.8188 | 266.0237 | 1143.9968 | 130.7099 | 3.3697 | 564.1394 | 17.2233 | 566.0189 | 2.6126 | 14.1316 | 2.8998 | 19.2865 | -92.5657 | 37.2909 | 2.87 | 321.38 | 3.52 | 4.1 | 29.5 | 371.37 | 221.7 | 2490.3668 | 396.33 | 374.38 | 4205.4286 | 2.65 | 566.29 | 6.15 | 163.45 | 83.0684
1116.5648 | 568.218 | 16.9542 | 566.5837 | 117.5576 | 16.7134 | 264.2529 | 1110.1379 | 130.3555 | 3.1148 | 564.5717 | 16.791 | 566.5837 | 2.5449 | 13.7253 | 2.8247 | 18.7667 | -92.5489 | 37.3407 | 2.8 | 322.24 | 3.39 | 3.82 | 26.5 | 370.74 | 212.26 | 2457.4504 | 384.4 | 363.24 | 4205.4286 | 2.58 | 566.41 | 5.96 | 162.56 | 85.1444
1046.2992 | 568.0972 | 16.3376 | 566.5515 | 119.1132 | 11.3122 | 260.9796 | 1045.0599 | 127.7294 | 3.456 | 564.5994 | 16.1959 | 566.5515 | 2.3867 | 12.8913 | 2.6522 | 18.0114 | -92.7086 | 36.9477 | 2.64 | 322.17 | 3.78 | 4.35 | 26.5 | 364.09 | 202.76 | 2507.5509 | 361 | 340.05 | 4205.4286 | 2.43 | 566.27 | 5.71 | 160.12 | 83.7841
1017.6448 | 568.1187 | 15.938 | 566.1219 | 103.5407 | 3.2203 | 259.6205 | 1017.7699 | 127.5167 | 3.5765 | 564.5556 | 15.7974 | 566.1219 | 2.3229 | 12.612 | 2.5833 | 17.6164 | -92.5383 | 37.1169 | 2.57 | 322.35 | 3.92 | 4.54 | 28.5 | 363.7 | 193.1 | 2453.6008 | 351.65 | 330.97 | 4205.4286 | 2.36 | 566.24 | 5.57 | 157.18 | 85.49
968.4238 | 568.5273 | 15.6061 | 566.6764 | 117.7332 | 4.1673 | 257.0917 | 967.9506 | 127.4326 | 3.4959 | 565.1102 | 15.4808 | 566.6764 | 2.2108 | 11.9865 | 2.4604 | 17.1384 | -92.5047 | 37.2177 | 2.45 | 322.18 | 3.98 | 4.26 | 25 | 362.89 | 189.74 | 2539.9905 | 333.92 | 314.15 | 4205.4286 | 2.25 | 566.42 | 5.4 | 153.24 | 83.2893
942.3001 | 568.2731 | 15.1302 | 566.5303 | 128.6706 | 3.5255 | 255.5403 | 941.9151 | 128.1273 | 3.449 | 564.6786 | 15.0048 | 566.5303 | 2.1532 | 11.6517 | 2.3968 | 16.5897 | -92.6632 | 36.5644 | 2.36 | 323.45 | 3.76 | 4.12 | 26.5 | 361.22 | 183.45 | 2559.9292 | 320.99 | 301.37 | 4205.4286 | 2.17 | 566.39 | 5.12 | 154.25 | 84.0592
910.9857 | 567.3775 | 14.7385 | 565.7484 | 96.711 | 2.5247 | 253.884 | 915.9689 | 127.9864 | 3.722 | 564.13 | 14.6238 | 565.7484 | 2.0827 | 11.2932 | 2.3206 | 16.263 | -92.6371 | 36.5965 | 2.31 | 323.01 | 3.85 | 4.71 | 25.5 | 361.45 | 175.21 | 2510.0771 | 313.16 | 293.55 | 4205.4286 | 2.12 | 565.48 | 5.06 | 151.85 | 85.1238
915.7937 | 567.1844 | 14.748 | 566.0818 | 92.731 | 4.7274 | 253.843 | 919.3437 | 127.1214 | 3.7411 | 563.9201 | 14.6312 | 566.0818 | 2.0931 | 11.3222 | 2.3309 | 16.2713 | -92.535 | 36.8066 | 2.31 | 323.17 | 4.16 | 4.72 | 27 | 362.22 | 179.35 | 2573.332 | 312.46 | 293.1 | 4205.4286 | 2.12 | 565.73 | 5.06 | 152.57 | 83.6787
950.0513 | 567.8645 | 15.1474 | 566.2657 | 98.1509 | 5.1615 | 255.2947 | 952.7387 | 128.3565 | 3.6436 | 564.6183 | 15.0266 | 566.2657 | 2.1697 | 11.7572 | 2.416 | 16.731 | -92.5879 | 36.5314 | 2.39 | 323.38 | 4.12 | 4.72 | 27 | 365.91 | 186.18 | 2560.5556 | 320.2 | 305.78 | 4205.4286 | 2.2 | 566.64 | 5.19 | 154.97 | 83.5012
960.7222 | 568.1131 | 15.1174 | 565.9378 | 85.5877 | 6.3192 | 255.593 | 960.7617 | 129.9025 | 3.5184 | 565.1119 | 14.9916 | 565.9378 | 2.1937 | 11.8884 | 2.4414 | 16.7607 | -92.455 | 36.8645 | 2.42 | 323.55 | 3.74 | 4.55 | 27.5 | 366.46 | 181.32 | 2466.5318 | 328.1 | 309.15 | 4205.4286 | 2.22 | 566.61 | 5.21 | 155.62 | 86.8858
965.4631 | 568.5584 | 15.3003 | 566.8102 | 95.6427 | 7.242 | 256.1734 | 967.8252 | 130.7372 | 3.6859 | 565.5092 | 15.1707 | 566.8102 | 2.2052 | 11.9448 | 2.4535 | 16.9205 | -92.5479 | 36.4681 | 2.44 | 323.04 | 4.07 | 4.73 | 27.5 | 365.66 | 184.91 | 2480.6233 | 332.85 | 313.48 | 4205.4286 | 2.25 | 566.74 | 5.33 | 156.13 | 85.4027
1006.7946 | 568.1778 | 15.8718 | 566.5431 | 100.7603 | 11.0847 | 258.4076 | 1001.9677 | 131.3796 | 3.5335 | 564.9029 | 15.7386 | 566.5431 | 2.2973 | 12.3889 | 2.5542 | 17.5276 | -92.4503 | 36.9545 | 2.54 | 322.94 | 3.89 | 4.42 | 27.5 | 366.3 | 189.38 | 2441.5207 | 345.98 | 326.2 | 4205.4286 | 2.34 | 566.84 | 5.49 | 158.85 | 86.9218
1025.3237 | 568.6193 | 16.0645 | 566.9759 | 102.946 | 12.5801 | 259.4999 | 1018.8573 | 130.2675 | 3.3311 | 565.2714 | 15.9294 | 566.9759 | 2.3405 | 12.5933 | 2.6017 | 17.757 | -92.2278 | 37.5253 | 2.59 | 322.7 | 3.5 | 3.91 | 28.5 | 366.71 | 194.06 | 2456.2994 | 352.02 | 332.25 | 4205.4286 | 2.38 | 566.87 | 5.6 | 159.65 | 86.5735
1041.3095 | 568.1051 | 16.2578 | 566.3674 | 81.4192 | 10.7739 | 260.397 | 1041.9334 | 131.292 | 3.2922 | 565.148 | 16.1147 | 566.3674 | 2.3753 | 12.8571 | 2.6406 | 18.0255 | -92.2422 | 37.4363 | 2.62 | 322.22 | 3.46 | 4.37 | 29.5 | 367.95 | 196.94 | 2451.0716 | 357.95 | 337.9 | 4205.4286 | 2.42 | 566.66 | 5.69 | 158.55 | 85.9492
1041.9136 | 567.1011 | 16.2372 | 566.5461 | 90.6153 | 14.8582 | 260.338 | 1039.5011 | 131.7871 | 3.3776 | 564.1728 | 16.0992 | 566.5461 | 2.3772 | 12.8277 | 2.6415 | 17.9782 | -92.2192 | 37.4926 | 2.62 | 322.37 | 3.46 | 4.43 | 29.5 | 371.37 | 197.77 | 2467.3162 | 357.28 | 337.09 | 4205.4286 | 2.42 | 566.8 | 5.65 | 160.21 | 85.8038
951.5112 | 568.3076 | 15.0416 | 567.0876 | 88.358 | 10.9011 | 255.3617 | 952.7588 | 130.8783 | 3.7697 | 565.268 | 14.9171 | 567.0876 | 2.1738 | 11.7611 | 2.4191 | 16.6731 | -92.4185 | 36.333 | 2.41 | 323.64 | 4.14 | 5.16 | 27.5 | 367.05 | 181.42 | 2478.7162 | 327.37 | 307.8 | 4205.4286 | 2.21 | 567.1 | 5.24 | 156.11 | 86.2246
982.4005 | 567.9137 | 15.4389 | 566.2114 | 96.2421 | 11.3235 | 257.2002 | 982.0971 | 128.9576 | 3.4776 | 565.0058 | 15.3087 | 566.2114 | 2.2441 | 12.1367 | 2.4961 | 17.065 | -92.2741 | 37.0004 | 2.47 | 323.29 | 3.51 | 4.9 | 30 | 365.91 | 188.49 | 2512.1418 | 335.25 | 315.54 | 4205.4286 | 2.27 | 566.55 | 5.33 | 157.09 | 85.3362
984.9206 | 568.722 | 15.4081 | 566.7054 | 130.2764 | 15.5264 | 257.2553 | 982.5788 | 128.4285 | 3.7179 | 565.455 | 15.2743 | 566.7054 | 2.2498 | 12.139 | 2.5018 | 16.9267 | -92.1197 | 37.4831 | 2.49 | 323.26 | 3.63 | 5.05 | 29 | 366.7 | 191.21 | 2536.7362 | 337.19 | 316.99 | 4205.4286 | 2.29 | 566.76 | 5.32 | 158.22 | 84.6366
930.315 | 567.5727 | 14.7074 | 566.6535 | 129.6321 | 9.2223 | 254.3559 | 930.1189 | 128.3122 | 3.6168 | 564.7972 | 14.5891 | 566.6535 | 2.1264 | 11.4927 | 2.3683 | 16.1506 | -92.4056 | 36.0086 | 2.36 | 324.3 | 3.94 | 4.77 | 27.5 | 363.69 | 179.13 | 2521.99 | 318.62 | 298.7 | 4205.4286 | 2.16 | 566.52 | 5.03 | 155.04 | 85.4192
936.5114 | 568.3532 | 14.8188 | 566.4638 | 109.9163 | 8.2662 | 254.6698 | 937.6394 | 128.1518 | 3.5646 | 565.123 | 14.6945 | 566.4638 | 2.14 | 11.5755 | 2.3819 | 16.319 | -92.0945 | 36.5254 | 2.36 | 323.8 | 3.75 | 4.67 | 29.5 | 363.36 | 177.62 | 2527.2494 | 318.19 | 298.3 | 4244.3333 | 2.16 | 566.27 | 5.06 | 154.71 | 85.8726
914.9525 | 567.6873 | 14.5693 | 566.2579 | 104.4579 | 4.0859 | 253.5936 | 914.8505 | 128.7743 | 3.8253 | 564.7596 | 14.4474 | 566.2579 | 2.0903 | 11.3316 | 2.3286 | 16.0735 | -92.0448 | 36.4551 | 2.32 | 324.14 | 3.62 | 4.93 | 27.5 | 364.05 | 176.97 | 2571.0069 | 312.11 | 292.15 | 4244.3333 | 2.12 | 566.5 | 5.01 | 153.63 | 84.3309
918.5482 | 568.0596 | 14.6721 | 565.5016 | 98.6476 | 3.8703 | 253.8296 | 919.8885 | 128.3011 | 3.5832 | 564.8232 | 14.5511 | 565.5016 | 2.0994 | 11.3851 | 2.3385 | 16.2055 | -92.0922 | 36.3293 | 2.32 | 323.81 | 3.66 | 4.77 | 27 | 365.08 | 176.84 | 2569.5581 | 312.44 | 292.1 | 4244.3333 | 2.12 | 566.05 | 5.03 | 151.62 | 84.5236
918.6784 | 568.398 | 14.6571 | 565.9286 | 70.945 | 1.724 | 253.9431 | 927.5317 | 127.9412 | 3.8263 | 564.9162 | 14.5336 | 565.9286 | 2.098 | 11.4656 | 2.3382 | 16.2954 | -92.2206 | 36.51 | 2.32 | 323.23 | 3.99 | 5.11 | 28 | 364.3 | 173.37 | 2503.6238 | 314.25 | 293.91 | 4244.3333 | 2.13 | 565.94 | 5.08 | 151.86 | 85.9397
939.6422 | 568.031 | 15.1389 | 566.6159 | 93.5557 | 8.8843 | 255.0715 | 938.6989 | 128.6423 | 3.7974 | 564.7802 | 15.0166 | 566.6159 | 2.1474 | 11.5954 | 2.3901 | 16.6844 | -92.7956 | 37.0027 | 2.38 | 322.82 | 3.98 | 5.05 | 25.5 | 363.64 | 182.47 | 2551.9425 | 323.84 | 303.48 | 4244.3333 | 2.18 | 566.41 | 5.22 | 153.94 | 83.7263
939.4035 | 568.4758 | 15.0364 | 566.4566 | 96.6551 | 4.7713 | 255.0932 | 941.3605 | 128.9881 | 3.6556 | 564.7874 | 14.9118 | 566.4566 | 2.1464 | 11.6282 | 2.3895 | 16.5954 | -92.6545 | 37.5033 | 2.38 | 323.09 | 3.96 | 4.78 | 28.5 | 363.26 | 181.37 | 2539.5709 | 323.06 | 303.12 | 4244.3333 | 2.18 | 566.48 | 5.19 | 154.91 | 84.0691
953.027 | 567.9244 | 15.1875 | 566.6723 | 82.9895 | 5.711 | 255.4767 | 946.8583 | 128.365 | 3.8064 | 564.5574 | 15.0641 | 566.6723 | 2.1774 | 11.6881 | 2.4236 | 16.7686 | -92.8923 | 36.9845 | 2.4 | 323.79 | 4.06 | 4.94 | 28 | 363.45 | 180.36 | 2529.4342 | 326.45 | 302.64 | 4244.3333 | 2.2 | 567.04 | 5.48 | 154.9 | 85.9597
1010.4224 | 568.5662 | 15.8039 | 567.0267 | 90.8063 | 7.2162 | 258.1543 | 984.7584 | 129.6034 | 3.7221 | 565.0818 | 15.6732 | 567.0267 | 2.3065 | 12.1609 | 2.5646 | 17.4166 | -93.0579 | 36.6089 | 2.54 | 325.55 | 3.54 | 5.08 | 28 | 369.25 | 192.12 | 2572.2259 | 344.03 | 317.01 | 4244.3333 | 2.33 | 567.3 | 5.84 | 158.82 | 85.7343
1010.9989 | 568.3469 | 15.851 | 566.9793 | 92.4506 | 4.7729 | 258.251 | 986.1208 | 129.5504 | 3.6354 | 565.021 | 15.7208 | 566.9793 | 2.3069 | 12.1946 | 2.5654 | 17.471 | -92.874 | 37.0403 | 2.55 | 325.25 | 3.4 | 5.11 | 29 | 369.02 | 192.59 | 2562.5134 | 345.88 | 318.99 | 4244.3333 | 2.35 | 567.25 | 5.9 | 159.04 | 85.4784
1043.4102 | 568.0909 | 16.1727 | 566.6213 | 101.4768 | 4.9593 | 259.9231 | 1019.8773 | 129.695 | 3.5981 | 564.688 | 16.0378 | 566.6213 | 2.382 | 12.6004 | 2.6465 | 17.8615 | -92.6407 | 37.4875 | 2.63 | 324.67 | 3.22 | 5 | 28.5 | 370.67 | 194.75 | 2508.6768 | 356.79 | 329.49 | 4244.3333 | 2.42 | 566.95 | 6.06 | 159.4 | 86.7746
1028.0322 | 568.056 | 16.1155 | 567.1216 | 99.9771 | 3.5449 | 259.0391 | 1006.8475 | 129.8991 | 3.7805 | 564.7972 | 15.9822 | 567.1216 | 2.3451 | 12.4222 | 2.6067 | 17.7426 | -92.8687 | 36.9346 | 2.58 | 324.67 | 3.81 | 5.15 | 28 | 368.92 | 191.07 | 2504.4463 | 350.68 | 323.81 | 4244.3333 | 2.38 | 567.17 | 5.99 | 158.77 | 87.2445
970.3609 | 567.511 | 15.3676 | 565.738 | 104.6665 | 7.6388 | 255.9717 | 950.218 | 132.0732 | 3.9382 | 564.1601 | 15.241 | 565.738 | 2.2163 | 11.7336 | 2.4648 | 16.8902 | -92.7921 | 37.1805 | 2.46 | 324.67 | 4.03 | 5 | 28 | 366.6 | 186.17 | 2579.8862 | 332.29 | 306.28 | 4244.3333 | 2.26 | 566.59 | 5.73 | 156.68 | 85.1565
914.4503 | 568.3299 | 14.5756 | 566.3627 | 95.4124 | 5.2825 | 253.0417 | 895.1605 | 128.0923 | 4.0315 | 564.9914 | 14.4632 | 566.3627 | 2.0906 | 11.0793 | 2.328 | 16.0514 | -92.9135 | 36.9883 | 2.33 | 326.29 | 3.72 | 5.02 | 28 | 365.99 | 174.13 | 2566.3788 | 313.37 | 287.98 | 4244.3333 | 2.13 | 567.1 | 5.47 | 154.77 | 86.4401
1022.5921 | 568.4758 | 15.8665 | 566.8584 | 89.3274 | 9.9727 | 258.7862 | 995.7508 | 128.7706 | 3.547 | 564.9431 | 15.7328 | 566.8584 | 2.3342 | 12.3384 | 2.5943 | 17.5347 | -92.6168 | 37.5047 | 2.58 | 325.15 | 2.8 | 4.37 | 28 | 369.52 | 192.28 | 2529.5243 | 349.1 | 322.63 | 4244.3333 | 2.38 | 567.24 | 5.9 | 159.54 | 86.9162
1029.4984 | 567.9871 | 16.0991 | 566.8477 | 81.0779 | 7.6474 | 259.182 | 1006.2056 | 128.8389 | 3.7078 | 564.8966 | 15.9655 | 566.8477 | 2.3491 | 12.454 | 2.6111 | 17.8063 | -92.6918 | 37.2505 | 2.58 | 324.5 | 3.23 | 4.65 | 28.5 | 371.67 | 190.48 | 2500.4968 | 350.04 | 323.32 | 4244.3333 | 2.37 | 567.37 | 5.97 | 159.75 | 87.9244
956.0772 | 567.8833 | 15.4706 | 566.6714 | 77.4812 | 3.6164 | 255.5782 | 955.0378 | 127.9775 | 3.6117 | 564.748 | 15.3502 | 566.6714 | 2.1829 | 11.7506 | 2.4292 | 17.0864 | -93.0138 | 36.5129 | 2.42 | 323.05 | 3.29 | 4.9 | 28.5 | 364.73 | 184.46 | 2558.1941 | 329.02 | 306.04 | 4244.3333 | 2.22 | 567.21 | 5.59 | 155.63 | 84.113
913.5235 | 568.5009 | 15.3056 | 567.007 | 85.1006 | 3.4998 | 253.3847 | 918.4746 | 128.7408 | 3.6652 | 565.1042 | 15.1979 | 567.007 | 2.0878 | 11.3248 | 2.3252 | 16.7873 | -92.8974 | 36.9138 | 2.31 | 321.51 | 3.78 | 4.84 | 27 | 361.59 | 179.52 | 2591.3775 | 313.78 | 294.03 | 4244.3333 | 2.11 | 567.36 | 5.23 | 152.71 | 82.7853
936.6416 | 568.2565 | 15.9624 | 567.0804 | 98.1408 | 7.8697 | 254.719 | 939.4482 | 134.3477 | 3.8093 | 565.0863 | 15.8528 | 567.0804 | 2.1406 | 11.5677 | 2.3822 | 17.4324 | -92.5991 | 37.6023 | 2.38 | 320.26 | 3.84 | 4.99 | 29.5 | 365.06 | 183.38 | 2572.2127 | 322.45 | 302.59 | 4244.3333 | 2.18 | 567.23 | 5.47 | 155.72 | 83.0286
881.2549 | 568.2959 | 14.8919 | 566.6043 | 98.3082 | 5.7895 | 251.9891 | 884.6897 | 132.9157 | 4.1224 | 564.9207 | 14.7843 | 566.6043 | 2.0161 | 10.9368 | 2.2452 | 16.3211 | -93.0315 | 36.5301 | 2.25 | 321.83 | 4.3 | 5.28 | 29 | 366.02 | 175.95 | 2606.4165 | 305.94 | 286.52 | 4244.3333 | 2.06 | 567.02 | 5.09 | 153.13 | 81.8904
889.7079 | 567.5772 | 14.9793 | 566.4879 | 77.5417 | 3.1397 | 252.2285 | 897.2575 | 130.6597 | 3.8513 | 564.5019 | 14.8727 | 566.4879 | 2.0353 | 11.0379 | 2.2676 | 16.4687 | -92.7976 | 37.1904 | 2.25 | 321.9 | 3.94 | 5 | 29 | 366.55 | 174.89 | 2596.1509 | 305.54 | 285.92 | 4244.3333 | 2.06 | 566.87 | 5.12 | 151.5 | 82.8009
879.271 | 568.1751 | 15.1347 | 566.7188 | 80.8003 | 4.7031 | 251.5734 | 883.105 | 128.3429 | 3.8941 | 565.225 | 15.0366 | 566.7188 | 2.0107 | 10.8769 | 2.2409 | 16.5729 | -92.9075 | 37.0112 | 2.23 | 321.77 | 3.78 | 5.18 | 27.5 | 364.44 | 172.45 | 2591.0131 | 301.75 | 282.49 | 4244.3333 | 2.04 | 567.01 | 5.12 | 151.66 | 83.2415
993.2031 | 567.672 | 16.5998 | 566.6159 | 88.2484 | 8.9441 | 257.7826 | 993.8179 | 131.6189 | 3.4179 | 564.4303 | 16.483 | 566.6159 | 2.2678 | 12.2336 | 2.5219 | 18.1786 | -92.6319 | 37.4318 | 2.5 | 320.01 | 3.48 | 4.69 | 28.5 | 369.46 | 194.86 | 2590.0376 | 339.5 | 319.32 | 4244.3333 | 2.29 | 567.21 | 5.67 | 157.29 | 82.4023
983.6249 | 568.1348 | 16.5136 | 566.7385 | 89.0692 | 11.2463 | 257.4026 | 984.8171 | 132.0125 | 3.5307 | 564.9521 | 16.4004 | 566.7385 | 2.2476 | 12.109 | 2.499 | 18.0607 | -92.7904 | 36.9412 | 2.49 | 319.93 | 3.7 | 4.67 | 29 | 370.03 | 194.17 | 2587.8358 | 338.61 | 318.46 | 4244.3333 | 2.28 | 566.89 | 5.67 | 157.87 | 81.9346
997.9892 | 568.2637 | 16.6143 | 567.1753 | 94.9567 | 11.1685 | 258.0449 | 1003.8796 | 132.7427 | 3.5744 | 564.8268 | 16.4934 | 567.1753 | 2.2791 | 12.3263 | 2.5339 | 18.1795 | -92.8724 | 36.5721 | 2.53 | 320 | 3.86 | 4.65 | 29 | 372.63 | 197.75 | 2586.5725 | 345.16 | 324.49 | 4244.3333 | 2.32 | 566.84 | 5.72 | 158.56 | 81.4586
1017.4558 | 568.423 | 16.8156 | 566.9489 | 101.2917 | 13.9885 | 259.126 | 1021.2451 | 134.727 | 3.4835 | 564.9315 | 16.696 | 566.9489 | 2.3227 | 12.5561 | 2.582 | 18.4249 | -92.556 | 37.3416 | 2.56 | 320.06 | 3.71 | 4.6 | 28.5 | 370.33 | 199.88 | 2584.4854 | 349.04 | 328.25 | 4244.3333 | 2.36 | 566.6 | 5.8 | 159.55 | 82.129
979.5549 | 567.7284 | 16.6841 | 566.4181 | 84.7425 | 9.1214 | 257.344 | 984.3604 | 130.851 | 3.699 | 564.5332 | 16.5724 | 566.4181 | 2.2382 | 12.0935 | 2.4891 | 18.2351 | -92.7306 | 37.0156 | 2.49 | 319.12 | 3.83 | 4.8 | 28.5 | 367.46 | 190.73 | 2543.9058 | 338.91 | 318.22 | 4244.3333 | 2.29 | 567.17 | 5.76 | 157.47 | 82.9914
939.3508 | 568.2368 | 15.9264 | 566.9148 | 88.4481 | 5.6001 | 255.0336 | 948.6997 | 129.9982 | 3.6955 | 564.8957 | 15.8135 | 566.9148 | 2.1469 | 11.652 | 2.389 | 17.438 | -92.8125 | 36.8711 | 2.37 | 320.28 | 3.83 | 5.06 | 29 | 364.32 | 183.23 | 2566.8004 | 323.27 | 302.98 | 4244.3333 | 2.18 | 567.37 | 5.46 | 154.72 | 82.9822
1047.102 | 568.1079 | 17.1467 | 567.0491 | 92.9058 | 17.3825 | 260.457 | 1045.3839 | 132.213 | 3.4077 | 564.791 | 17.0133 | 567.0491 | 2.3896 | 12.8579 | 2.6534 | 18.7879 | -92.4962 | 37.3676 | 2.63 | 319.88 | 3.17 | 4.63 | 29.5 | 370.62 | 209.04 | 2630.6385 | 358.32 | 337.27 | 4244.3333 | 2.42 | 567.37 | 5.94 | 160.63 | 80.8717
1014.7435 | 568.3397 | 17.0334 | 566.9166 | 101.0827 | 15.4327 | 259.0673 | 1012.9793 | 134.12 | 3.5744 | 564.8303 | 16.9143 | 566.9166 | 2.3172 | 12.4449 | 2.5754 | 18.5726 | -92.5516 | 37.2332 | 2.55 | 319.75 | 3.62 | 4.97 | 29.5 | 366.47 | 207.04 | 2696.7003 | 346.8 | 325.86 | 4244.3333 | 2.34 | 567.55 | 5.84 | 159.16 | 79.2881
1012.5334 | 568.4893 | 16.9864 | 566.7806 | 89.6158 | 12.9127 | 259.1057 | 1015.7546 | 135.7725 | 3.44 | 564.9682 | 16.8611 | 566.7806 | 2.3121 | 12.4896 | 2.5697 | 18.5739 | -92.4807 | 37.4224 | 2.56 | 319.7 | 3.24 | 5.04 | 29.5 | 373.21 | 212.99 | 2752.407 | 349.51 | 328.44 | 4244.3333 | 2.36 | 567.49 | 5.87 | 159.6 | 76.7641
991.7742 | 568.6146 | 16.4605 | 566.6597 | 75.401 | 9.2289 | 257.9332 | 999.1407 | 134.1928 | 3.4351 | 565.089 | 16.3355 | 566.6597 | 2.2644 | 12.2942 | 2.5178 | 18.0903 | -92.5077 | 37.3956 | 2.51 | 320.23 | 3.48 | 4.71 | 29.5 | 371 | 193.63 | 2585.6748 | 341.48 | 320.96 | 4286 | 2.3 | 567.18 | 5.71 | 157.54 | 81.7936
1019.6349 | 568.3648 | 16.6461 | 566.8656 | 77.1915 | 15.5167 | 259.2834 | 1022.0365 | 132.5145 | 3.6118 | 565.0818 | 16.514 | 566.8656 | 2.3279 | 12.5727 | 2.5873 | 18.3114 | -92.6011 | 37.0048 | 2.58 | 321.06 | 3.7 | 4.95 | 29 | 372.75 | 197.72 | 2560.9015 | 351.9 | 330.91 | 4286 | 2.37 | 567.83 | 5.79 | 159.88 | 82.5483
1043.6179 | 568.3442 | 17.2267 | 567.1959 | 91.1642 | 17.8142 | 260.4896 | 1047.053 | 135.8462 | 3.3227 | 564.8241 | 17.0942 | 567.1959 | 2.3817 | 12.8696 | 2.6456 | 18.8742 | -92.3473 | 37.4955 | 2.61 | 319.56 | 3.62 | 4.63 | 28.5 | 370.4 | 198.83 | 2548.2488 | 355.42 | 334.42 | 4286 | 2.4 | 567.55 | 5.94 | 160.25 | 83.6044
1006.5136 | 567.6631 | 16.7582 | 566.3743 | 94.7086 | 13.2971 | 258.434 | 1009.5674 | 135.6968 | 3.5722 | 564.4142 | 16.6324 | 566.3743 | 2.2982 | 12.4307 | 2.5546 | 18.352 | -92.5726 | 36.9716 | 2.54 | 319.55 | 4.06 | 4.79 | 29 | 369.05 | 195.09 | 2565.6032 | 346.46 | 325.91 | 4286 | 2.34 | 567.15 | 5.8 | 157.72 | 82.4542
1065.9021 | 567.4984 | 17.5438 | 566.385 | 89.045 | 13.4694 | 261.733 | 1069.7358 | 137.5884 | 3.4212 | 564.1528 | 17.4083 | 566.385 | 2.4316 | 13.1568 | 2.7005 | 19.2564 | -92.5628 | 37.4665 | 2.68 | 318.73 | 3.63 | 4.78 | 28.5 | 371.18 | 202.13 | 2503.4798 | 367.06 | 346.05 | 4286 | 2.47 | 567 | 6.13 | 160.91 | 83.6754
1068.9647 | 567.2979 | 17.512 | 565.9429 | 81.3678 | 10.585 | 261.6935 | 1075.7364 | 134.849 | 3.3106 | 564.135 | 17.3748 | 565.9429 | 2.4372 | 13.2262 | 2.7076 | 19.2428 | -92.5671 | 37.9081 | 2.68 | 318.9 | 2.96 | 4.53 | 29 | 369.08 | 200.08 | 2476.086 | 366.96 | 346.33 | 4286 | 2.47 | 567.06 | 6.09 | 160.91 | 84.7114
1063.4037 | 568.048 | 17.5231 | 566.1478 | 71.7537 | 11.4492 | 261.5586 | 1074.3836 | 132.3298 | 3.5636 | 564.6093 | 17.3874 | 566.1478 | 2.4257 | 13.1512 | 2.6945 | 19.2726 | -92.5636 | 37.8792 | 2.68 | 318.23 | 3.33 | 4.81 | 30.5 | 371.12 | 199.7 | 2467.6071 | 367.57 | 346.86 | 4286 | 2.47 | 566.8 | 6.15 | 160.83 | 84.3623
1028.491 | 567.784 | 17.2283 | 566.453 | 86.2701 | 7.9543 | 259.7107 | 1042.4765 | 130.8636 | 3.2628 | 564.3515 | 17.0992 | 566.453 | 2.3466 | 12.7619 | 2.609 | 18.8821 | -92.5639 | 37.9412 | 2.6 | 318.14 | 3.27 | 4.57 | 30.5 | 365.73 | 196.36 | 2514.4124 | 355.09 | 334.71 | 4286 | 2.39 | 566.79 | 5.98 | 158.97 | 83.0179
1022.3565 | 568.0005 | 17.1413 | 566.2105 | 87.2123 | 9.3423 | 259.5108 | 1027.7606 | 130.3691 | 3.2644 | 564.5448 | 17.0158 | 566.2105 | 2.3339 | 12.6388 | 2.5945 | 18.7628 | -92.7563 | 37.4802 | 2.59 | 318.51 | 3.38 | 4.56 | 27 | 368.93 | 197.76 | 2544.7321 | 353.5 | 333.08 | 4286 | 2.38 | 567.08 | 5.95 | 159.49 | 82.3166
1038.1622 | 567.7974 | 17.2153 | 566.7627 | 95.0424 | 16.1755 | 260.3404 | 1037.2687 | 134.606 | 3.4479 | 564.4383 | 17.0852 | 566.7627 | 2.3686 | 12.7678 | 2.6317 | 18.8367 | -92.8652 | 37.075 | 2.62 | 319.54 | 3.36 | 4.77 | 29.5 | 370.75 | 199.7 | 2534.2399 | 358.58 | 337.74 | 4286 | 2.41 | 567.27 | 5.97 | 160.8 | 83.1548
932.2957 | 568.0292 | 15.9844 | 566.0073 | 102.2949 | 7.6323 | 254.8418 | 936.8607 | 134.9255 | 3.4914 | 564.5377 | 15.8747 | 566.0073 | 2.131 | 11.5184 | 2.372 | 17.4237 | -92.8682 | 37.2556 | 2.36 | 320.3 | 3.54 | 4.49 | 28 | 363.69 | 179.52 | 2558.6868 | 320.69 | 300.71 | 4286 | 2.17 | 566.36 | 5.45 | 155.49 | 83.4313
934.6484 | 568.5743 | 15.9977 | 567.2057 | 110.466 | 9.8828 | 254.9929 | 939.0281 | 133.6578 | 3.6579 | 565.0263 | 15.89 | 567.2057 | 2.1355 | 11.5507 | 2.3762 | 17.4396 | -92.7888 | 37.106 | 2.38 | 320.44 | 3.56 | 4.85 | 29 | 365.01 | 185.51 | 2631.4607 | 322.5 | 302.15 | 4286 | 2.18 | 566.76 | 5.49 | 155.47 | 81.0341
1007.6388 | 567.8537 | 16.8859 | 566.5112 | 91.8203 | 9.797 | 259.0083 | 1012.2054 | 133.8672 | 3.492 | 564.3784 | 16.7602 | 566.5112 | 2.2996 | 12.4445 | 2.5575 | 18.4776 | -92.6814 | 37.1153 | 2.54 | 319.35 | 3.46 | 4.76 | 27.5 | 367.98 | 196.77 | 2597.1798 | 345.65 | 324.72 | 4286 | 2.33 | 566.65 | 5.83 | 158.03 | 81.6264
998.6805 | 567.9298 | 16.784 | 566.3376 | 96.2226 | 18.3814 | 258.4594 | 998.7602 | 132.6551 | 3.4278 | 564.3417 | 16.663 | 566.3376 | 2.2818 | 12.2735 | 2.5359 | 18.321 | -92.5573 | 37.4181 | 2.52 | 319.67 | 3.22 | 4.59 | 29 | 369.33 | 200.61 | 2671.3097 | 342.24 | 321.87 | 4286 | 2.32 | 565.97 | 5.75 | 158.93 | 79.0394
1040.4468 | 568.7524 | 17.2966 | 566.6428 | 98.3015 | 19.2 | 260.5772 | 1035.9609 | 136.8361 | 3.4919 | 564.8599 | 17.1656 | 566.6428 | 2.3745 | 12.7626 | 2.6384 | 18.9034 | -92.4386 | 37.6372 | 2.63 | 319.41 | 3.4 | 4.68 | 28.5 | 374.3 | 206.69 | 2630.7339 | 357.73 | 336.74 | 4286 | 2.42 | 566.15 | 5.98 | 160.75 | 80.5829
992.4189 | 567.7821 | 16.8145 | 566.3366 | 101.436 | 11.3374 | 258.2716 | 995.2946 | 132.5108 | 3.267 | 564.4195 | 16.6951 | 566.3366 | 2.2663 | 12.2273 | 2.5201 | 18.338 | -92.5349 | 37.4795 | 2.51 | 319.66 | 3.12 | 4.63 | 29 | 367.91 | 197.25 | 2633.9331 | 341.35 | 320.97 | 4286 | 2.31 | 566.67 | 5.78 | 158.35 | 80.3862
950.8169 | 567.5978 | 16.1591 | 566.2678 | 111.6785 | 13.4078 | 255.8535 | 951.6753 | 132.6762 | 3.2738 | 564.1788 | 16.0455 | 566.2678 | 2.1735 | 11.7055 | 2.4177 | 17.5902 | -92.6183 | 37.2901 | 2.4 | 320.46 | 2.97 | 4.58 | 28.5 | 365.58 | 188.06 | 2639.5034 | 325.27 | 305.37 | 4286 | 2.2 | 566.55 | 5.51 | 156.67 | 81.3763
964.5148 | 568.108 | 16.4241 | 566.1827 | 96.6296 | 10.1442 | 256.4385 | 966.1303 | 134.0355 | 3.4537 | 564.5753 | 16.3107 | 566.1827 | 2.2024 | 11.8729 | 2.4506 | 17.9 | -92.6739 | 37.0879 | 2.44 | 320.15 | 3.33 | 4.63 | 28.5 | 366.96 | 184.8 | 2545.2386 | 331.06 | 311.19 | 4286 | 2.24 | 566.4 | 5.63 | 157.14 | 83.7336
966.0925 | 567.7894 | 16.4528 | 566.4898 | 104.5688 | 14.9721 | 256.6221 | 965.0565 | 132.7675 | 3.4623 | 564.4267 | 16.3402 | 566.4898 | 2.2076 | 11.8714 | 2.4553 | 17.9223 | -92.4908 | 37.4298 | 2.43 | 320.11 | 3.19 | 4.36 | 26.5 | 366.8 | 188.29 | 2608.731 | 329.14 | 309.35 | 4286 | 2.23 | 566.65 | 5.59 | 157.35 | 82.5194
1008.5036 | 568.7139 | 16.9036 | 566.8129 | 98.8435 | 15.6378 | 258.8415 | 1013.8003 | 134.1365 | 3.3653 | 565.0227 | 16.7799 | 566.8129 | 2.3023 | 12.4286 | 2.559 | 18.4812 | -92.5086 | 37.3379 | 2.54 | 319.73 | 2.97 | 4.17 | 28.5 | 367.67 | 191.04 | 2523.8031 | 344.75 | 324.43 | 4286 | 2.33 | 566.64 | 5.84 | 159.2 | 84.4756
1008.2703 | 568.0408 | 16.8635 | 566.5077 | 93.2549 | 12.7701 | 258.7954 | 1012.0828 | 133.8473 | 3.4326 | 564.5753 | 16.7389 | 566.5077 | 2.3019 | 12.439 | 2.5588 | 18.4512 | -92.6029 | 37.3777 | 2.59 | 319.37 | 3.14 | 4.2 | 30 | 369.2 | 194.85 | 2504.2043 | 353.62 | 333.49 | 4286 | 2.39 | 566.81 | 5.95 | 159.86 | 82.8678
1007.4995 | 568.0272 | 16.8713 | 566.5229 | 94.021 | 12.65 | 258.758 | 1011.4725 | 133.8208 | 3.4289 | 564.5611 | 16.7471 | 566.5229 | 2.3001 | 12.4303 | 2.5569 | 18.4546 | -92.6009 | 37.3842 | 2.46 | 319.04 | 3.05 | 4.39 | 28.5 | 364.75 | 185.76 | 2532.1779 | 334.01 | 314.42 | 4286 | 2.26 | 566.55 | 5.72 | 156.62 | 86.4189
1005.6928 | 568.0143 | 16.8721 | 566.4888 | 94.8923 | 12.4643 | 258.671 | 1009.6216 | 133.892 | 3.4251 | 564.5359 | 16.7487 | 566.4888 | 2.296 | 12.4082 | 2.5525 | 18.4489 | -92.5931 | 37.4082 | 2.47 | 319.66 | 3.27 | 4.76 | 26.5 | 367.54 | 188.16 | 2555.7083 | 335.12 | 315.55 | 4286 | 2.27 | 566.52 | 5.71 | 157.48 | 85.2749
1003.4625 | 568.0063 | 16.8491 | 566.456 | 95.2452 | 12.4155 | 258.5647 | 1007.1825 | 133.8959 | 3.4243 | 564.5288 | 16.7262 | 566.456 | 2.2911 | 12.3782 | 2.547 | 18.4209 | -92.6053 | 37.3893 | 2.53 | 319.92 | 3.2 | 4.71 | 28.5 | 370.48 | 191.64 | 2539.8715 | 343.21 | 323.39 | 4286 | 2.32 | 566.48 | 5.78 | 158.74 | 83.7658
1001.8909 | 568.031 | 16.8385 | 566.4444 | 95.4305 | 12.3897 | 258.4942 | 1005.5326 | 133.8359 | 3.4113 | 564.5393 | 16.7161 | 566.4444 | 2.2875 | 12.3574 | 2.5431 | 18.4054 | -92.6091 | 37.3947 | 2.48 | 319.82 | 3.26 | 4.49 | 29.5 | 367.7 | 191.41 | 2590.1659 | 336.51 | 316.73 | 4286 | 2.28 | 566.63 | 5.71 | 157.83 | 83.658
994.2987 | 568.0619 | 16.7411 | 566.4542 | 95.6823 | 12.1466 | 258.0956 | 997.8492 | 133.7023 | 3.4229 | 564.5747 | 16.62 | 566.4542 | 2.2704 | 12.2648 | 2.5244 | 18.2953 | -92.6068 | 37.3847 | 2.26 | 321.72 | 3.58 | 5.23 | 27 | 364.86 | 178.3 | 2675.4676 | 304.96 | 285.63 | 4286 | 2.07 | 566.72 | 5.18 | 153.67 | 88.7234
986.399 | 568.0936 | 16.645 | 566.493 | 96.4053 | 11.9172 | 257.6935 | 989.8718 | 133.5687 | 3.4314 | 564.608 | 16.5251 | 566.493 | 2.2527 | 12.1684 | 2.505 | 18.1844 | -92.6071 | 37.3533 | 2.33 | 321.03 | 3.7 | 5.1 | 28.5 | 363.54 | 181.04 | 2617.6077 | 315.81 | 296.43 | 4286 | 2.14 | 566.76 | 5.35 | 154.65 | 86.8722
984.0683 | 568.0975 | 16.6203 | 566.4772 | 97.5953 | 12.285 | 257.5676 | 986.726 | 133.7339 | 3.4281 | 564.6173 | 16.5009 | 566.4772 | 2.2475 | 12.1356 | 2.4993 | 18.1515 | -92.597 | 37.3446 | 2.52 | 319.41 | 3.34 | 4.86 | 29.5 | 367.67 | 193.09 | 2571.094 | 342.23 | 321.88 | 4286 | 2.32 | 566.66 | 5.81 | 158.42 | 81.7532
980.4303 | 568.1011 | 16.5711 | 566.4818 | 97.8721 | 12.2373 | 257.3823 | 982.721 | 133.99 | 3.4434 | 564.6325 | 16.4525 | 566.4818 | 2.2391 | 12.0895 | 2.4902 | 18.0962 | -92.5982 | 37.3068 | 2.37 | 320.25 | 3.77 | 4.99 | 29.5 | 362.22 | 180.45 | 2574.6819 | 320.52 | 300.39 | 4286 | 2.17 | 566.8 | 5.49 | 155.26 | 86.8301
975.6137 | 568.0831 | 16.5109 | 566.4693 | 98.3616 | 11.9792 | 257.1354 | 978.0072 | 133.9942 | 3.4617 | 564.6361 | 16.3928 | 566.4693 | 2.2282 | 12.0334 | 2.4784 | 18.0283 | -92.5895 | 37.2998 | 2.35 | 320 | 3.57 | 4.79 | 29 | 361.11 | 179.71 | 2568.4843 | 319.38 | 299.88 | 4286 | 2.16 | 566.4 | 5.45 | 154.15 | 86.7439
972.3426 | 568.1152 | 16.4761 | 566.4849 | 98.4624 | 11.8387 | 256.9686 | 974.5515 | 133.8387 | 3.4726 | 564.6721 | 16.3588 | 566.4849 | 2.2209 | 11.9949 | 2.4704 | 17.988 | -92.5722 | 37.3137 | 2.36 | 320.72 | 3.89 | 4.97 | 29.5 | 362.52 | 180.66 | 2582.6649 | 319.19 | 299.81 | 4286 | 2.16 | 566.81 | 5.42 | 154.63 | 86.1793
928.3435 | 568.0614 | 15.7176 | 565.8686 | 83.0451 | 7.7906 | 254.5944 | 925.927 | 131.6404 | 3.3376 | 564.8617 | 15.6061 | 565.8686 | 2.1157 | 11.4849 | 2.3627 | 17.2183 | -92.4212 | 37.7266 | 2.36 | 321.13 | 3.27 | 4.66 | 28 | 364.82 | 178.54 | 2570.9931 | 317.57 | 298.5 | 4298.4286 | 2.16 | 566.16 | 5.39 | 153.89 | 83.6163
999.815 | 567.5414 | 16.7933 | 566.2158 | 84.6554 | 4.9744 | 258.5979 | 1005.3552 | 134.8332 | 3.1019 | 564.4106 | 16.6658 | 566.2158 | 2.2815 | 12.43 | 2.5376 | 18.4183 | -92.2523 | 37.9203 | 2.53 | 318.71 | 2.82 | 4.54 | 28.5 | 367.62 | 190.58 | 2534.3228 | 343.51 | 323.24 | 4298.4286 | 2.32 | 566.28 | 5.83 | 157.76 | 83.3543
1002.3196 | 567.656 | 16.9641 | 566.1022 | 87.3692 | 6.7382 | 258.6853 | 1001.0566 | 134.0545 | 3.3134 | 564.3381 | 16.8399 | 566.1022 | 2.2875 | 12.41 | 2.5452 | 18.5623 | -92.5191 | 37.1666 | 2.54 | 318.8 | 3.37 | 4.65 | 29.5 | 366.68 | 193.89 | 2561.3815 | 345.6 | 325.38 | 4298.4286 | 2.33 | 566.68 | 5.87 | 158.56 | 82.3369
988.2094 | 567.6246 | 16.7557 | 566.1335 | 103.6377 | 9.7115 | 257.8486 | 984.718 | 133.5749 | 3.4671 | 564.3855 | 16.6322 | 566.1335 | 2.2564 | 12.2184 | 2.5087 | 18.2915 | -92.5352 | 37.1703 | 2.49 | 318.97 | 3.8 | 4.5 | 28.5 | 363.11 | 190.81 | 2575.7903 | 338.47 | 318.42 | 4298.4286 | 2.29 | 566.49 | 5.75 | 158.01 | 82.7455
1006.8545 | 568.0417 | 16.7703 | 566.3778 | 94.2759 | 6.4249 | 258.8506 | 1007.4681 | 134.1073 | 3.4646 | 564.8411 | 16.6425 | 566.3778 | 2.2975 | 12.5116 | 2.5553 | 18.4034 | -92.5024 | 37.4991 | 2.54 | 319.15 | 3.66 | 4.6 | 29 | 367.93 | 192.4 | 2543.2611 | 345.81 | 325.18 | 4298.4286 | 2.33 | 566.37 | 5.84 | 157.69 | 83.2706
937.6335 | 568.4714 | 16.1292 | 565.4784 | 92.5235 | 4.8597 | 255.0253 | 940.5013 | 134.7921 | 3.4188 | 565.1543 | 16.0207 | 565.4784 | 2.1419 | 11.6634 | 2.3843 | 17.6431 | -92.7777 | 37.0026 | 2.37 | 319.52 | 3.27 | 4.88 | 28.5 | 367.65 | 184.99 | 2627.1725 | 322.75 | 302.67 | 4298.4286 | 2.18 | 565.83 | 5.53 | 154.12 | 81.186
971.5915 | 568.3156 | 16.5283 | 566.1711 | 87.1844 | 8.4054 | 257.1401 | 965.3562 | 132.0965 | 3.4011 | 564.8948 | 16.4049 | 566.1711 | 2.218 | 12.0224 | 2.4691 | 18.0725 | -92.8254 | 37.1811 | 2.46 | 319.7 | 3.17 | 4.76 | 28.5 | 369 | 186.96 | 2555.682 | 334.55 | 314.45 | 4298.4286 | 2.25 | 566.67 | 5.68 | 157.05 | 83.2842
1004.1422 | 567.9137 | 16.9536 | 566.5085 | 89.2306 | 17.2662 | 258.643 | 992.3874 | 133.6222 | 3.3472 | 564.799 | 16.8339 | 566.5085 | 2.2928 | 12.3552 | 2.5477 | 18.5369 | -92.7447 | 37.5757 | 2.53 | 319.68 | 3.2 | 4.79 | 29 | 373.16 | 192.52 | 2546.5703 | 345 | 324.96 | 4298.4286 | 2.33 | 566.96 | 5.85 | 159.29 | 83.82
1045.1398 | 567.3159 | 17.4646 | 566.2257 | 72.0799 | 15.2615 | 260.7322 | 1035.6442 | 137.0007 | 3.2647 | 564.1314 | 17.3361 | 566.2257 | 2.3847 | 12.8647 | 2.6493 | 19.1731 | -92.7283 | 37.5141 | 2.63 | 318.93 | 3.03 | 4.71 | 29.5 | 376.55 | 199.46 | 2529.6213 | 359.71 | 338.93 | 4298.4286 | 2.42 | 566.81 | 6.05 | 160.42 | 83.5659
1047.725 | 567.9773 | 17.466 | 566.1129 | 76.095 | 14.578 | 261.0558 | 1037.2519 | 136.5506 | 3.2325 | 564.8348 | 17.3304 | 566.1129 | 2.3919 | 12.9112 | 2.6581 | 19.1677 | -92.7852 | 37.3227 | 2.64 | 318.78 | 2.94 | 4.61 | 29.5 | 376.2 | 200.97 | 2537.765 | 361.27 | 340.4 | 4298.4286 | 2.43 | 566.55 | 6.07 | 160.55 | 83.1836
1042.5112 | 567.9459 | 17.2081 | 566.7376 | 73.3294 | 15.6133 | 260.5552 | 1033.6121 | 134.4065 | 3.2989 | 564.7749 | 17.0786 | 566.7376 | 2.3793 | 12.8485 | 2.6429 | 18.9345 | -92.7998 | 37.2295 | 2.64 | 319.78 | 3.01 | 4.62 | 30 | 374.04 | 200.76 | 2532.4349 | 361.42 | 340.76 | 4298.4286 | 2.43 | 567.03 | 6.01 | 160.88 | 82.9292
1044.5664 | 567.3713 | 17.3598 | 566.9837 | 81.0438 | 16.1369 | 260.6108 | 1034.1373 | 136.1844 | 3.1802 | 564.4303 | 17.2346 | 566.9837 | 2.3833 | 12.8437 | 2.6485 | 19.0367 | -92.5565 | 37.9023 | 2.62 | 319.04 | 2.93 | 4.57 | 29.5 | 371.41 | 196.75 | 2507.0875 | 357.59 | 337.33 | 4298.4286 | 2.41 | 566.97 | 6.03 | 160.11 | 84.6801
1050.9085 | 568.6548 | 17.4332 | 566.2651 | 86.607 | 19.5846 | 261.0006 | 1036.441 | 141.0139 | 3.6149 | 565.1114 | 17.3097 | 566.2651 | 2.399 | 12.8871 | 2.6642 | 19.1222 | -92.55 | 37.9412 | 2.65 | 319.49 | 3.47 | 5.08 | 29 | 377.09 | 193.87 | 2451.6382 | 360.58 | 339.91 | 4298.4286 | 2.44 | 566.74 | 6.05 | 160.94 | 86.8189
959.4559 | 567.2237 | 16.4892 | 565.0058 | 83.111 | 6.5868 | 256.1686 | 952.9501 | 140.5064 | 3.7021 | 564.1985 | 16.3825 | 565.0058 | 2.1913 | 11.8587 | 2.4384 | 18.0659 | -92.941 | 37.0719 | 2.44 | 319.36 | 3.55 | 4.96 | 26 | 373.45 | 181.3 | 2501.9427 | 331.3 | 311.48 | 4298.4286 | 2.23 | 566 | 5.68 | 154.22 | 84.913
966.6629 | 568.0623 | 16.4096 | 565.874 | 77.2452 | 6.907 | 256.6762 | 960.0377 | 140.0438 | 3.4053 | 564.8581 | 16.295 | 565.874 | 2.2068 | 11.9707 | 2.4563 | 18.0165 | -92.8431 | 37.2152 | 2.44 | 319.48 | 3.27 | 4.74 | 28.5 | 374.32 | 183.44 | 2520.3891 | 332.64 | 312.85 | 4298.4286 | 2.24 | 566.44 | 5.66 | 156.48 | 84.4371
981.1977 | 568.3228 | 16.7396 | 566.7135 | 76.8789 | 9.5209 | 257.4662 | 973.3415 | 138.5763 | 3.3691 | 565.0801 | 16.6245 | 566.7135 | 2.2407 | 12.1183 | 2.4924 | 18.3451 | -92.6867 | 37.6082 | 2.48 | 319.2 | 3.08 | 4.71 | 29 | 376.3 | 186.59 | 2527.8738 | 337.43 | 317.28 | 4298.4286 | 2.28 | 566.93 | 5.78 | 157.42 | 84.2753
991.3805 | 567.8045 | 16.7991 | 566.5327 | 86.2035 | 14.5998 | 257.9017 | 982.0347 | 136.0321 | 3.1617 | 564.8724 | 16.6786 | 566.5327 | 2.2638 | 12.2184 | 2.518 | 18.3821 | -92.6895 | 37.6421 | 2.51 | 319.53 | 2.75 | 4.65 | 28.5 | 374.26 | 191.56 | 2567.6104 | 340.98 | 320.69 | 4298.4286 | 2.3 | 566.93 | 5.79 | 158.46 | 83.0974
965.0634 | 568.1285 | 16.4251 | 566.2669 | 87.1128 | 14.0941 | 256.4249 | 957.2659 | 137.7089 | 3.2903 | 565.08 | 16.3074 | 566.2669 | 2.2047 | 11.9238 | 2.4522 | 17.9709 | -92.9049 | 37.085 | 2.45 | 319.84 | 3.1 | 4.65 | 27.5 | 374.04 | 185.63 | 2553.3353 | 332.53 | 312.5 | 4298.4286 | 2.24 | 566.75 | 5.63 | 157.3 | 83.717
954.4529 | 567.9298 | 16.1834 | 566.3617 | 76.8933 | 10.3698 | 256.0106 | 946.6695 | 139.3246 | 3.4461 | 564.8411 | 16.0693 | 566.3617 | 2.1805 | 11.7848 | 2.4263 | 17.7476 | -93.0689 | 36.5967 | 2.42 | 320.32 | 3.56 | 4.87 | 27 | 373.22 | 181.59 | 2528.2663 | 328.84 | 308.73 | 4298.4286 | 2.21 | 566.66 | 5.56 | 156.13 | 84.6148
991.3588 | 567.7096 | 16.7515 | 566.4888 | 79.2968 | 13.7621 | 257.9714 | 984.0189 | 138.6411 | 3.3333 | 564.4867 | 16.629 | 566.4888 | 2.2639 | 12.2287 | 2.517 | 18.3732 | -92.8893 | 37.0345 | 2.51 | 319.4 | 3.12 | 4.78 | 28.5 | 375.56 | 186.81 | 2500.1228 | 341.39 | 321.18 | 4298.4286 | 2.3 | 566.93 | 5.79 | 158.63 | 85.131
989.0557 | 567.9325 | 16.8468 | 566.0709 | 85.4526 | 14.0312 | 257.8831 | 978.1837 | 138.6378 | 3.3859 | 564.7757 | 16.7258 | 566.0709 | 2.2589 | 12.1857 | 2.5118 | 18.4241 | -92.7283 | 37.4354 | 2.5 | 319.02 | 3.22 | 4.82 | 28.5 | 376.23 | 188.43 | 2532.7649 | 339.62 | 319.79 | 4298.4286 | 2.29 | 566.53 | 5.79 | 157.7 | 84.3012
928.3249 | 568.4167 | 15.8289 | 566.0655 | 100.213 | 11.645 | 254.4792 | 922.384 | 137.2427 | 3.4704 | 565.2519 | 15.7185 | 566.0655 | 2.1216 | 11.4705 | 2.3618 | 17.302 | -92.9182 | 37.0372 | 2.36 | 320.57 | 3.22 | 4.83 | 29 | 373.03 | 179.36 | 2559.0538 | 320.4 | 301.27 | 4298.4286 | 2.16 | 566.65 | 5.45 | 155.51 | 83.6049
894.1034 | 568.3711 | 15.2882 | 566.8441 | 98.8994 | 8.5621 | 252.7874 | 887.1295 | 135.5156 | 3.5143 | 565.2232 | 15.1831 | 566.8441 | 2.045 | 11.0667 | 2.2777 | 16.7176 | -92.881 | 37.1536 | 2.28 | 321.42 | 3.32 | 4.67 | 28.5 | 370.62 | 172.42 | 2564.3924 | 308.06 | 289.01 | 4298.4286 | 2.08 | 567.23 | 5.22 | 154.59 | 84.0779
885.7464 | 568.0337 | 15.1718 | 566.0047 | 95.2616 | 6.9083 | 252.2922 | 881.6214 | 133.2581 | 3.482 | 564.8849 | 15.0648 | 566.0047 | 2.0254 | 10.997 | 2.2577 | 16.5916 | -92.8887 | 37.1218 | 2.25 | 321.23 | 3.22 | 4.6 | 26.5 | 367.46 | 169.52 | 2557.5431 | 303.68 | 284.91 | 4298.4286 | 2.05 | 566.28 | 5.16 | 152.42 | 84.4717
1033.99 | 567.1422 | 16.6815 | 566.1174 | 91.9077 | 17.7776 | 259.6392 | 1023.5273 | 138.4659 | 3.2639 | 563.879 | 16.5416 | 566.1174 | 2.3597 | 12.7662 | 2.6225 | 18.3846 | -92.7385 | 37.3148 | 2.6 | 320.91 | 2.83 | 4.48 | 28.5 | 375.26 | 194.94 | 2509.6911 | 354.83 | 333.88 | 4298.4286 | 2.39 | 566.9 | 5.74 | 158.98 | 85.0796
960.1689 | 567.7231 | 16.3955 | 566.6571 | 92.1915 | 10.2772 | 256.3183 | 957.8244 | 139.9015 | 3.432 | 564.6514 | 16.2826 | 566.6571 | 2.1937 | 11.8351 | 2.4398 | 17.921 | -92.8766 | 37.1175 | 2.43 | 319.21 | 3.16 | 4.52 | 29 | 370.17 | 182.9 | 2524.6711 | 330.66 | 311.4 | 4298.4286 | 2.23 | 566.82 | 5.64 | 156.99 | 84.2403
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
966.4645 | 568.1353 | 15.5664 | 566.2492 | 102.9975 | 8.1827 | 256.4305 | 968.7554 | 130.9194 | 3.6972 | 564.6683 | 15.4377 | 566.2492 | 2.2068 | 11.9813 | 2.456 | 17.1225 | -92.8257 | 37.0505 | 2.4397 | 321.8651 | 3.6978 | 4.5457 | 29.2631 | 365.1762 | 183.0495 | 2505.5278 | 333.2974 | 312.9657 | 4279.7901 | 2.2384 | 566.4826 | 5.3866 | 155.5789 | 84.9381
978.7954 | 568.6853 | 16.4639 | 566.7743 | 121.4484 | 12.0551 | 256.5838 | 970.0959 | 128.829 | 3.7058 | 565.1606 | 16.3452 | 566.7743 | 2.2357 | 12.0375 | 2.4885 | 17.8795 | -93.0477 | 36.1113 | 2.47 | 319.97 | 3.79 | 3.72 | 29.5 | 369.04 | 191.87 | 2578.2688 | 338.02 | 318.15 | 4275.1667 | 2.3 | 565.17 | 5.71 | 157.65 | 82.0855
949.1027 | 567.9772 | 16.0635 | 565.8588 | 117.2413 | 13.6478 | 254.9305 | 940.0225 | 128.8417 | 3.8205 | 564.5395 | 15.9503 | 565.8588 | 2.1675 | 11.6803 | 2.4124 | 17.4359 | -92.8809 | 36.6378 | 2.41 | 320.42 | 3.95 | 3.8 | 29 | 368.25 | 182.77 | 2537.0875 | 327.28 | 307.98 | 4275.1667 | 2.24 | 564.62 | 5.59 | 156.08 | 83.739
975.1811 | 567.4689 | 16.5147 | 566.5201 | 131.0079 | 16.7049 | 256.4529 | 964.8443 | 132.5282 | 3.5263 | 564.2191 | 16.4046 | 566.5201 | 2.2278 | 11.985 | 2.4774 | 17.9043 | -92.5619 | 37.3777 | 2.48 | 319.56 | 3.58 | 3.54 | 28.5 | 370.03 | 189.3 | 2552.2377 | 336.45 | 317.09 | 4275.1667 | 2.31 | 565.07 | 5.74 | 157.91 | 82.8711
994.471 | 567.7902 | 16.6582 | 566.0637 | 127.5232 | 19.3957 | 257.4172 | 983.4836 | 132.3605 | 3.4649 | 564.4026 | 16.5461 | 566.0637 | 2.2709 | 12.2245 | 2.5253 | 18.0903 | -92.6488 | 37.0995 | 2.5 | 319.43 | 3.64 | 3.85 | 28.5 | 369.03 | 193.39 | 2576.103 | 340.67 | 320.94 | 4275.1667 | 2.33 | 564.95 | 5.79 | 157.97 | 82.5008
984.0154 | 567.1046 | 16.514 | 565.1884 | 124.4512 | 21.7719 | 256.9197 | 977.0671 | 132.7118 | 3.6121 | 563.5971 | 16.4002 | 565.1884 | 2.2479 | 12.1083 | 2.4994 | 17.9318 | -92.5646 | 37.3538 | 2.49 | 319.47 | 3.68 | 3.85 | 29.5 | 372.01 | 192.67 | 2583.9023 | 338.24 | 318.78 | 4275.1667 | 2.31 | 565.1 | 5.79 | 157.69 | 81.9038
986.5107 | 567.7329 | 16.6484 | 566.5667 | 134.064 | 26.3578 | 256.9638 | 969.3037 | 134.2694 | 3.326 | 564.4455 | 16.5427 | 566.5667 | 2.2545 | 12.0634 | 2.5051 | 18.0203 | -92.3076 | 38.0367 | 2.49 | 320.08 | 2.89 | 3.77 | 29.5 | 374.62 | 194.87 | 2622.2906 | 337.08 | 317.7 | 4275.1667 | 2.31 | 565.24 | 5.76 | 158.33 | 81.6176
897.3923 | 567.1968 | 15.3307 | 566.0529 | 119.1593 | 12.6186 | 252.2531 | 892.2426 | 130.3587 | 3.8849 | 564.0204 | 15.2285 | 566.0529 | 2.052 | 11.0999 | 2.2854 | 16.6316 | -92.9047 | 36.6674 | 2.28 | 320.93 | 3.88 | 3.96 | 27.5 | 368.02 | 181.01 | 2663.6649 | 309.34 | 290.52 | 4275.1667 | 2.12 | 564.95 | 5.3 | 154.17 | 80.1997
960.0201 | 567.681 | 16.1358 | 566.8943 | 122.5657 | 14.9008 | 255.7947 | 954.7739 | 130.6138 | 3.6264 | 564.143 | 16.0194 | 566.8943 | 2.193 | 11.866 | 2.44 | 17.5366 | -92.6569 | 37.1854 | 2.43 | 319.79 | 4.14 | 3.8 | 28.5 | 368.73 | 191.27 | 2637.4375 | 329.33 | 310.04 | 4275.1667 | 2.25 | 564.98 | 5.64 | 156.63 | 80.7679
983.6373 | 567.4733 | 16.5396 | 565.788 | 115.4903 | 15.1368 | 257.1646 | 977.7995 | 128.9725 | 3.6052 | 564.0526 | 16.4217 | 565.788 | 2.2472 | 12.1303 | 2.4998 | 17.9898 | -92.6406 | 37.1204 | 2.48 | 319.48 | 3.56 | 3.74 | 29 | 368.2 | 195.95 | 2631.8533 | 337.96 | 318.3 | 4275.1667 | 2.31 | 564.7 | 5.76 | 157.72 | 80.5059
933.8425 | 567.1825 | 15.8319 | 566.0825 | 126.513 | 17.3264 | 254.6305 | 924.6816 | 126.7531 | 3.6203 | 563.8736 | 15.7267 | 566.0825 | 2.1363 | 11.5029 | 2.3766 | 17.1718 | -92.6899 | 37.1283 | 2.38 | 320.46 | 3.19 | 3.83 | 30 | 365.68 | 188.11 | 2652.8174 | 322.63 | 303.15 | 4275.1667 | 2.21 | 564.64 | 5.53 | 155.92 | 80.0886
943.5107 | 567.4286 | 16.0218 | 565.7102 | 126.0285 | 20.1417 | 254.6881 | 931.3638 | 125.0182 | 3.4628 | 564.2146 | 15.913 | 565.7102 | 2.1567 | 11.5876 | 2.3996 | 17.3758 | -92.4127 | 37.8004 | 2.38 | 320.5 | 3.11 | 3.74 | 29 | 366.52 | 191.62 | 2717.6468 | 320.71 | 301.44 | 4275.1667 | 2.2 | 564.66 | 5.49 | 155.19 | 79.4465
945.445 | 567.8833 | 15.6638 | 566.1979 | 133.627 | 21.1024 | 254.7589 | 933.1848 | 125.9049 | 3.4286 | 564.544 | 15.5549 | 566.1979 | 2.1604 | 11.6199 | 2.4035 | 17.0405 | -92.5346 | 37.4939 | 2.38 | 321.51 | 2.96 | 3.53 | 29 | 368.6 | 177.8 | 2526.4459 | 321.2 | 301.54 | 4284.7273 | 2.18 | 565.89 | 5.29 | 155.93 | 86.6187
999.2167 | 567.4662 | 15.8833 | 565.9205 | 127.862 | 26.3728 | 257.8293 | 982.4112 | 128.692 | 3.3493 | 564.1403 | 15.7528 | 565.9205 | 2.2821 | 12.2885 | 2.5367 | 17.397 | -92.4473 | 37.6088 | 2.53 | 322.49 | 3.15 | 3.54 | 29.5 | 372.29 | 186.25 | 2470.8355 | 343.12 | 322.98 | 4284.7273 | 2.32 | 566.62 | 5.45 | 158.56 | 87.2351
966.2041 | 567.6139 | 15.5836 | 566.7752 | 128.2458 | 20.8231 | 256.0361 | 952.2452 | 127.7964 | 3.4761 | 564.3023 | 15.4578 | 566.7752 | 2.2075 | 11.8852 | 2.4548 | 17.0416 | -92.5482 | 37.4326 | 2.46 | 322.53 | 3.22 | 3.58 | 28 | 370.75 | 178.54 | 2436.4457 | 333.6 | 313.98 | 4284.7273 | 2.26 | 567.37 | 5.35 | 157.67 | 88.1352
951.9452 | 568.0883 | 15.243 | 566.3143 | 117.5781 | 15.4651 | 255.336 | 939.5736 | 126.583 | 3.4724 | 564.5601 | 15.1123 | 566.3143 | 2.1741 | 11.7656 | 2.42 | 16.7101 | -92.6713 | 37.1738 | 2.41 | 322.87 | 3.16 | 3.85 | 28 | 368.79 | 173.17 | 2413.1988 | 326.6 | 307.47 | 4284.7273 | 2.21 | 566.59 | 5.23 | 156.43 | 89.2185
917.9221 | 567.5325 | 14.8416 | 566.5595 | 121.5346 | 16.6625 | 253.5524 | 906.6442 | 126.9765 | 3.6718 | 563.8853 | 14.724 | 566.5595 | 2.0989 | 11.3331 | 2.3365 | 16.247 | -92.7922 | 37.1218 | 2.33 | 323.31 | 3.38 | 3.92 | 27.5 | 369.22 | 171.59 | 2482.4133 | 315.5 | 296.17 | 4284.7273 | 2.13 | 566.79 | 5.04 | 155.55 | 87.19
940.7612 | 567.7598 | 15.1097 | 566.7036 | 118.6344 | 13.124 | 255.0162 | 929.0341 | 130.1635 | 3.7113 | 564.1708 | 14.9865 | 566.7036 | 2.1437 | 11.6289 | 2.3933 | 16.5722 | -92.793 | 37.3019 | 2.39 | 322.97 | 3.59 | 3.8 | 29 | 365.32 | 175.26 | 2464.9312 | 324.04 | 304.65 | 4284.7273 | 2.19 | 566.8 | 5.18 | 156.37 | 87.1923
842.486 | 567.7329 | 13.3273 | 565.6771 | 109.8038 | 7.4031 | 249.2203 | 848.2054 | 129.0616 | 4.4675 | 564.0983 | 13.2046 | 565.6771 | 1.9282 | 10.611 | 2.1515 | 14.743 | -92.7548 | 37.4168 | 2.15 | 324.73 | 4.69 | 4.75 | 29 | 359.88 | 157.6 | 2478.248 | 291.31 | 272.48 | 4284.7273 | 1.96 | 566.52 | 4.61 | 150.1 | 87.2031
976.6349 | 567.8699 | 15.7027 | 566.0404 | 130.1311 | 11.4801 | 256.8702 | 968.4552 | 130.61 | 3.7222 | 564.424 | 15.5708 | 566.0404 | 2.2311 | 12.0964 | 2.4814 | 17.2029 | -92.6832 | 37.8661 | 2.47 | 321.72 | 3.02 | 3.93 | 29.5 | 364.53 | 178.95 | 2419.8446 | 336.64 | 316.86 | 4284.7273 | 2.27 | 566.68 | 5.4 | 157.5 | 88.1752
967.6517 | 567.2639 | 15.3573 | 565.9446 | 126.715 | 13.5426 | 256.3981 | 957.0784 | 129.9322 | 3.7019 | 563.8897 | 15.2218 | 565.9446 | 2.2097 | 11.9919 | 2.4591 | 16.8535 | -92.7667 | 37.6436 | 2.45 | 322.29 | 2.9 | 3.87 | 29.5 | 364.89 | 177.79 | 2419.5066 | 334.37 | 314.85 | 4284.7273 | 2.25 | 567.04 | 5.33 | 157.3 | 88.2268
900.2503 | 567.6023 | 14.4772 | 565.5625 | 120.9929 | 5.203 | 252.8638 | 900.3115 | 129.3964 | 3.7564 | 564.1457 | 14.3492 | 565.5625 | 2.0581 | 11.2714 | 2.293 | 15.8887 | -92.9582 | 37.1963 | 2.29 | 322.66 | 3.8 | 3.99 | 30 | 358.79 | 169.14 | 2474.4563 | 311.74 | 292.88 | 4284.7273 | 2.09 | 566.11 | 4.96 | 152.89 | 86.1102
891.1586 | 567.8037 | 14.4376 | 565.6297 | 121.9328 | 7.19 | 252.2618 | 887.7108 | 129.0442 | 3.7992 | 564.1368 | 14.3105 | 565.6297 | 2.0384 | 11.1191 | 2.2709 | 15.8122 | -92.9546 | 37.1898 | 2.27 | 322.95 | 3.85 | 4.06 | 28 | 360.87 | 167.19 | 2474.9129 | 308.63 | 289.45 | 4284.7273 | 2.08 | 565.93 | 4.93 | 153.18 | 86.4886
882.8017 | 567.8188 | 14.1646 | 564.9477 | 114.6067 | 4.3355 | 251.735 | 881.7127 | 128.7784 | 3.8211 | 564.1045 | 14.0384 | 564.9477 | 2.0191 | 11.0425 | 2.2506 | 15.5762 | -93.1527 | 36.6356 | 2.24 | 323.36 | 3.86 | 4.08 | 26.5 | 361.65 | 163.47 | 2446.1283 | 305.29 | 286.34 | 4284.7273 | 2.05 | 565.58 | 4.84 | 152 | 87.5052
870.2228 | 567.1521 | 13.9695 | 566.0243 | 120.8037 | 4.4784 | 251.1711 | 868.8668 | 126.9398 | 3.9735 | 563.8674 | 13.8479 | 566.0243 | 1.9896 | 10.8902 | 2.2185 | 15.3359 | -93.124 | 36.7708 | 2.21 | 323.88 | 3.74 | 4.15 | 26 | 359.86 | 159.37 | 2423.3692 | 300.54 | 281.78 | 4284.7273 | 2.02 | 566.44 | 4.75 | 151.57 | 88.6158
866.379 | 567.6246 | 13.9549 | 566.0789 | 110.436 | 4.521 | 250.8944 | 864.9842 | 127.8924 | 3.9602 | 564.1994 | 13.8362 | 566.0789 | 1.9813 | 10.8308 | 2.2092 | 15.3469 | -93.2755 | 36.3027 | 2.22 | 324.16 | 4.04 | 4.29 | 27 | 360.22 | 158.53 | 2404.6227 | 301.08 | 282.48 | 4284.7273 | 2.03 | 566.32 | 4.77 | 151.8 | 88.8627
962.1651 | 567.3123 | 15.4547 | 565.8811 | 118.4021 | 11.1712 | 256.1792 | 955.9125 | 128.8911 | 3.6648 | 563.8817 | 15.3212 | 565.8811 | 2.1985 | 11.9529 | 2.4468 | 16.9639 | -92.8284 | 37.2614 | 2.44 | 322.13 | 3.14 | 3.84 | 27.5 | 364.04 | 173.12 | 2370.3329 | 331.9 | 312.94 | 4284.7273 | 2.23 | 566.12 | 5.3 | 156.48 | 89.5831
986.9736 | 567.6506 | 15.7025 | 566.1285 | 112.8338 | 11.2809 | 257.5285 | 982.5778 | 130.2923 | 3.5977 | 564.1907 | 15.5656 | 566.1285 | 2.2537 | 12.2805 | 2.5071 | 17.2668 | -92.5489 | 37.9268 | 2.5 | 321.64 | 2.96 | 3.82 | 29 | 365.9 | 176.27 | 2355.6512 | 339.97 | 320.62 | 4284.7273 | 2.29 | 566.21 | 5.45 | 158.01 | 90.0426
952.1274 | 568.0728 | 15.2624 | 566.1361 | 105.2347 | 14.0402 | 255.5577 | 949.9465 | 128.8016 | 3.6492 | 564.4291 | 15.1382 | 566.1361 | 2.175 | 11.8345 | 2.421 | 16.7934 | -92.8426 | 37.2399 | 2.42 | 321.98 | 2.95 | 3.84 | 29 | 365.33 | 170.47 | 2358.5439 | 328.59 | 309.69 | 4284.7273 | 2.21 | 565.91 | 5.26 | 155.53 | 90.1509
962.1713 | 567.247 | 15.4226 | 566.1317 | 100.9332 | 8.8626 | 256.2744 | 955.8132 | 128.1077 | 3.7971 | 563.9587 | 15.2941 | 566.1317 | 2.1913 | 11.955 | 2.4454 | 16.9881 | -92.768 | 37.4795 | 2.44 | 321.68 | 3.31 | 3.94 | 26.5 | 365.05 | 167.36 | 2297.9297 | 331.3 | 312.06 | 4284.7273 | 2.23 | 566.03 | 5.33 | 156.7 | 92.7716
969.1303 | 567.2756 | 15.5876 | 565.4158 | 94.0656 | 6.276 | 256.7685 | 965.3516 | 130.4047 | 3.8541 | 564.0321 | 15.4546 | 565.4158 | 2.2128 | 12.0804 | 2.4623 | 17.195 | -92.488 | 38.1316 | 2.46 | 321.08 | 3.52 | 3.99 | 26.5 | 364.45 | 169.92 | 2316.3783 | 333.66 | 314.31 | 4284.7273 | 2.25 | 565.44 | 5.42 | 156.27 | 91.7012
923.0522 | 567.579 | 14.8859 | 565.66 | 101.0124 | 5.1612 | 254.15 | 920.7397 | 128.6086 | 3.9249 | 564.024 | 14.7579 | 565.66 | 2.1097 | 11.5081 | 2.3499 | 16.3941 | -92.933 | 37.0424 | 2.35 | 322.32 | 3.42 | 4.06 | 27.5 | 362.49 | 169.8 | 2429.5288 | 318.68 | 299.46 | 4284.7273 | 2.14 | 565.69 | 5.13 | 153.91 | 87.7452
924.0596 | 567.5342 | 14.966 | 566.2677 | 106.6775 | 8.1076 | 254.3281 | 916.9352 | 129.5085 | 3.7874 | 563.9407 | 14.8379 | 566.2677 | 2.1134 | 11.481 | 2.3529 | 16.4437 | -92.717 | 37.5865 | 2.34 | 322.16 | 3.56 | 3.87 | 28 | 362.78 | 170.03 | 2442.0346 | 317.57 | 298.33 | 4284.7273 | 2.14 | 565.83 | 5.13 | 154.15 | 87.8893
978.8233 | 567.8699 | 15.6772 | 566.189 | 101.1532 | 8.4935 | 257.3658 | 967.9024 | 131.3745 | 3.9244 | 564.2388 | 15.5398 | 566.189 | 2.2344 | 12.127 | 2.4858 | 17.2601 | -92.934 | 36.8118 | 2.48 | 322.04 | 3.41 | 4.04 | 28.5 | 367.36 | 177.31 | 2395.3243 | 337.55 | 317.17 | 4284.7273 | 2.27 | 566.14 | 5.42 | 157.2 | 89.0506
933.7123 | 567.366 | 15.0611 | 565.5482 | 104.607 | 5.6352 | 254.5414 | 926.6644 | 130.307 | 3.7967 | 564.3328 | 14.9343 | 565.5482 | 2.1317 | 11.5922 | 2.3723 | 16.5631 | -92.562 | 37.8886 | 2.37 | 323.01 | 3.17 | 3.88 | 28.5 | 363.95 | 170.56 | 2428.2399 | 320.67 | 300.96 | 4284.7273 | 2.17 | 566.39 | 5.18 | 154.96 | 88.5507
913.694 | 568.5618 | 14.6784 | 565.7299 | 106.3682 | 10.8458 | 253.4512 | 904.878 | 128.5448 | 3.8226 | 565.1185 | 14.5533 | 565.7299 | 2.0882 | 11.3429 | 2.3265 | 16.1643 | -92.5386 | 37.9781 | 2.33 | 323.18 | 3.63 | 3.93 | 27 | 363.25 | 169.55 | 2455.5535 | 314.8 | 295.85 | 4284.7273 | 2.13 | 565.87 | 5.08 | 154.38 | 87.5415
944.3817 | 567.8493 | 15.0308 | 566.3519 | 107.8135 | 13.5366 | 255.0559 | 931.8904 | 132.1311 | 3.8002 | 564.3891 | 14.8968 | 566.3519 | 2.1573 | 11.6803 | 2.4011 | 16.5484 | -92.682 | 37.5359 | 2.38 | 323.13 | 3.57 | 3.94 | 28 | 365.74 | 175.5 | 2474.8869 | 322.83 | 303.84 | 4284.7273 | 2.18 | 565.71 | 5.15 | 155.6 | 87.3262
1070.2573 | 567.9692 | 16.5732 | 566.0834 | 111.0072 | 23.2486 | 262.3193 | 1054.3874 | 134.9133 | 3.7275 | 564.4025 | 16.4163 | 566.0834 | 2.4433 | 13.1936 | 2.7125 | 18.2725 | -92.4745 | 37.7723 | 2.7 | 321.65 | 3.28 | 3.83 | 29 | 374.16 | 197.28 | 2426.3477 | 367.99 | 348.38 | 4284.7273 | 2.48 | 566.03 | 5.79 | 161.31 | 87.1878
1076.4227 | 567.2272 | 16.8978 | 566.5166 | 126.9731 | 27.2316 | 262.4886 | 1062.085 | 134.2875 | 3.7157 | 563.973 | 16.7444 | 566.5166 | 2.4556 | 13.2612 | 2.7267 | 18.5621 | -92.3782 | 37.9581 | 2.71 | 321 | 3.3 | 3.82 | 28.5 | 372.82 | 193.3 | 2369.9147 | 369.42 | 349.48 | 4284.7273 | 2.49 | 566.19 | 5.86 | 161.82 | 89.5288
1047.9761 | 567.826 | 16.4374 | 565.9975 | 111.1102 | 19.4344 | 261.2539 | 1043.1363 | 133.4179 | 3.4289 | 564.3873 | 16.2806 | 565.9975 | 2.3916 | 13.0268 | 2.6563 | 18.1427 | -92.6003 | 37.4347 | 2.64 | 320.95 | 2.75 | 3.64 | 29 | 371.21 | 189.37 | 2380.5158 | 360.86 | 340.85 | 4284.7273 | 2.43 | 566.38 | 5.74 | 160.57 | 88.7757
1047.0989 | 568.4212 | 16.4274 | 566.5881 | 103.9277 | 22.5249 | 261.1768 | 1036.2067 | 133.1614 | 3.5282 | 564.8491 | 16.2774 | 566.5881 | 2.3893 | 12.9785 | 2.6536 | 18.1238 | -92.2741 | 38.2614 | 2.64 | 321.19 | 2.87 | 3.61 | 29 | 371.63 | 188.2 | 2371.8621 | 359.78 | 339.98 | 4284.7273 | 2.43 | 566.53 | 5.74 | 160.75 | 89.5092
974.7006 | 567.3489 | 15.4676 | 565.8301 | 99.792 | 18.903 | 257.1196 | 956.6884 | 133.5539 | 3.7252 | 563.8853 | 15.3326 | 565.8301 | 2.2272 | 12.0141 | 2.4765 | 17.0461 | -92.3989 | 38.0642 | 2.46 | 323.13 | 2.98 | 3.7 | 29 | 372.1 | 176.43 | 2409.5701 | 332.93 | 313.73 | 4284.7273 | 2.26 | 566.13 | 5.32 | 157.37 | 89.7928
940.3551 | 567.5343 | 15.0594 | 565.2967 | 98.774 | 14.0935 | 255.3845 | 930.1751 | 131.9395 | 3.7576 | 563.9998 | 14.9313 | 565.2967 | 2.1481 | 11.6686 | 2.3912 | 16.6117 | -92.4662 | 37.9442 | 2.39 | 322.93 | 3.2 | 3.74 | 28.5 | 368.52 | 174.21 | 2457.9898 | 322.59 | 303.68 | 4284.7273 | 2.18 | 565.68 | 5.19 | 155.63 | 87.5955
1019.6907 | 566.957 | 16.1179 | 565.822 | 112.2826 | 25.1149 | 259.7358 | 1004.4049 | 135.0545 | 3.661 | 563.6633 | 15.9731 | 565.822 | 2.3281 | 12.5732 | 2.5869 | 17.7584 | -92.1523 | 38.4683 | 2.58 | 321.92 | 2.97 | 3.4 | 28 | 372.55 | 192.54 | 2505.0608 | 348.98 | 329.27 | 4284 | 2.37 | 566.24 | 5.58 | 159.97 | 85.7755
948.8206 | 567.835 | 15.2352 | 566.214 | 98.5549 | 17.1096 | 256.0221 | 933.3076 | 133.4554 | 3.7226 | 564.2728 | 15.1061 | 566.214 | 2.1683 | 11.7252 | 2.4132 | 16.7723 | -92.7441 | 37.1666 | 2.41 | 322.66 | 3.42 | 3.49 | 26 | 365.19 | 180.75 | 2516.1105 | 326.99 | 307.75 | 4284 | 2.21 | 566.13 | 5.25 | 156.85 | 85.4037
946.9142 | 568.0337 | 15.0697 | 566.6974 | 97.4099 | 15.2995 | 255.8132 | 934.0714 | 133.7462 | 3.7484 | 564.3766 | 14.9396 | 566.6974 | 2.1634 | 11.7236 | 2.4082 | 16.6105 | -92.4685 | 37.8603 | 2.4 | 322.94 | 3.39 | 3.51 | 27.5 | 366.42 | 184.64 | 2595.0519 | 324.04 | 304.81 | 4284 | 2.2 | 566.33 | 5.2 | 156.56 | 83.3751
967.9369 | 567.6926 | 15.6172 | 565.737 | 102.6328 | 23.5057 | 256.9401 | 947.0115 | 134.772 | 3.7751 | 564.0759 | 15.4946 | 565.737 | 2.2122 | 11.8708 | 2.4598 | 17.1543 | -92.6583 | 37.2477 | 2.46 | 322.65 | 3.6 | 3.61 | 28 | 370.46 | 186.75 | 2555.3756 | 332.26 | 313.08 | 4284 | 2.25 | 566.08 | 5.35 | 158.26 | 84.5227
911.0096 | 567.613 | 14.56 | 566.351 | 98.5501 | 12.0462 | 253.8137 | 896.1957 | 135.7454 | 3.8258 | 563.9587 | 14.439 | 566.351 | 2.0833 | 11.2622 | 2.3198 | 16.0595 | -92.7949 | 37.4123 | 2.31 | 323.99 | 4 | 3.69 | 28.5 | 364.15 | 173.7 | 2532.0906 | 312.72 | 293.88 | 4284 | 2.12 | 566.32 | 5.01 | 154.86 | 85.4685
913.4553 | 567.3678 | 14.6245 | 566.2087 | 98.1485 | 9.9757 | 253.911 | 901.4353 | 137.1863 | 3.7123 | 563.8907 | 14.5013 | 566.2087 | 2.0872 | 11.3184 | 2.3262 | 16.1272 | -92.9077 | 37.3668 | 2.31 | 323.65 | 3.62 | 3.65 | 28.5 | 366.21 | 171.92 | 2499.1696 | 313.38 | 294.7 | 4284 | 2.12 | 566.42 | 5.02 | 154.79 | 86.3485
897.851 | 568.005 | 14.445 | 566.3232 | 91.5729 | 10.4132 | 253.1639 | 885.1889 | 137.4435 | 3.8737 | 564.3166 | 14.3213 | 566.3232 | 2.0527 | 11.1521 | 2.2873 | 15.9431 | -92.9698 | 36.2427 | 2.28 | 323.66 | 3.49 | 3.94 | 29 | 369.84 | 166.29 | 2457.0978 | 308.64 | 289.93 | 4284 | 2.08 | 566.24 | 4.95 | 153.98 | 88.0717
893.4556 | 567.7956 | 14.2391 | 566.1729 | 89.2206 | 13.4037 | 252.8285 | 879.7847 | 134.1471 | 3.7667 | 564.1582 | 14.1161 | 566.1729 | 2.0427 | 11.0697 | 2.2757 | 15.7356 | -92.571 | 37.0258 | 2.28 | 324.51 | 3.16 | 3.82 | 28 | 370.88 | 169.28 | 2517.6029 | 306.92 | 288.05 | 4284 | 2.08 | 566.36 | 4.91 | 154.45 | 86.3407
896.0501 | 567.2684 | 14.7385 | 565.814 | 93.4011 | 15.9292 | 252.9709 | 879.3021 | 134.0724 | 3.7773 | 563.9757 | 14.6187 | 565.814 | 2.0506 | 11.0671 | 2.2824 | 16.1666 | -92.3637 | 37.6103 | 2.29 | 323.02 | 3.22 | 3.78 | 28 | 369.1 | 169.98 | 2527.3117 | 307.13 | 288.13 | 4284 | 2.09 | 565.75 | 5.04 | 154.63 | 86.2477
912.5285 | 567.6398 | 14.7508 | 566.0037 | 95.6316 | 17.884 | 253.8526 | 897.7418 | 133.898 | 3.5864 | 564.1144 | 14.6291 | 566.0037 | 2.0879 | 11.2809 | 2.3238 | 16.2317 | -92.4508 | 37.4954 | 2.32 | 323.47 | 3.04 | 3.63 | 28.5 | 371.52 | 174.38 | 2549.9861 | 311.93 | 292.96 | 4284 | 2.12 | 566.09 | 5.03 | 155.6 | 85.5641
885.0428 | 567.5503 | 14.1213 | 566.1174 | 89.6036 | 9.4881 | 252.5025 | 875.7399 | 132.3865 | 3.7134 | 564.0544 | 13.9958 | 566.1174 | 2.0237 | 11.028 | 2.2549 | 15.619 | -92.4744 | 37.3849 | 2.25 | 324.19 | 3.1 | 3.81 | 27.5 | 368.13 | 166.12 | 2512.6508 | 302.05 | 283.23 | 4284 | 2.05 | 566.3 | 4.85 | 153.4 | 86.8284
885.1916 | 568.1975 | 14.022 | 565.6484 | 95.2911 | 7.4669 | 252.3213 | 874.1337 | 133.4628 | 3.7138 | 564.3587 | 13.8896 | 565.6484 | 2.0236 | 11.0124 | 2.2552 | 15.5082 | -92.2794 | 37.6869 | 2.25 | 324.8 | 3.44 | 3.81 | 27 | 367.82 | 166.37 | 2522.4883 | 301.25 | 282.55 | 4284 | 2.05 | 566.24 | 4.82 | 153 | 86.7489
868.1242 | 567.3168 | 13.6907 | 566.0897 | 93.4556 | 7.1649 | 251.3235 | 855.7887 | 133.8841 | 3.702 | 563.7385 | 13.5661 | 566.0897 | 1.9865 | 10.78 | 2.2137 | 15.1678 | -92.6808 | 37.3205 | 2.21 | 325.68 | 3.7 | 3.85 | 28 | 365.82 | 165.58 | 2545.0996 | 297.24 | 278.71 | 4284 | 2.02 | 566.27 | 4.7 | 152.62 | 85.5764
869.5997 | 568.3362 | 13.7527 | 566.6562 | 87.5099 | 5.8342 | 251.6112 | 857.6066 | 138.502 | 3.8154 | 564.3703 | 13.6214 | 566.6562 | 1.9903 | 10.8205 | 2.2182 | 15.2379 | -92.4786 | 37.5517 | 2.22 | 325.42 | 4.02 | 3.87 | 28.5 | 365.27 | 164.96 | 2527.0468 | 298.26 | 279.65 | 4284 | 2.03 | 566.81 | 4.75 | 152.9 | 86.0586
897.2187 | 567.3713 | 14.3804 | 565.4005 | 92.216 | 9.011 | 253.0365 | 888.9816 | 139.7076 | 3.8309 | 563.9658 | 14.2553 | 565.4005 | 2.0518 | 11.1886 | 2.2845 | 15.8985 | -92.5012 | 37.0915 | 2.28 | 323.68 | 3.91 | 3.92 | 29 | 368.58 | 168.07 | 2500.9965 | 307.3 | 287.89 | 4284 | 2.08 | 566.1 | 4.95 | 153.73 | 86.7468
905.8825 | 567.9549 | 14.2158 | 566.2597 | 94.2114 | 14.8864 | 253.1794 | 892.7961 | 135.3062 | 3.7831 | 564.2262 | 14.0841 | 566.2597 | 2.0712 | 11.2337 | 2.3069 | 15.7288 | -92.2249 | 37.8965 | 2.3 | 324.79 | 3.75 | 3.67 | 28 | 369.81 | 166.35 | 2455.2744 | 309.08 | 290.25 | 4284 | 2.11 | 566.38 | 4.9 | 154.34 | 89.0083
885.5791 | 567.0912 | 14.361 | 565.0998 | 98.5328 | 12.8423 | 252.1306 | 874.5186 | 132.7977 | 3.7913 | 563.3707 | 14.244 | 565.0998 | 2.0257 | 10.995 | 2.2561 | 15.7789 | -92.3656 | 37.1422 | 2.26 | 323.7 | 3.81 | 3.66 | 27.5 | 366.67 | 161.84 | 2439.8162 | 302.54 | 284.17 | 4284 | 2.06 | 565.7 | 4.89 | 153.46 | 89.3546
905.5168 | 567.6855 | 14.7728 | 566.0216 | 85.0637 | 7.2022 | 253.5992 | 904.2597 | 132.8655 | 3.5355 | 563.9524 | 14.6502 | 566.0216 | 2.069 | 11.3386 | 2.3058 | 16.2893 | -92.3078 | 37.5749 | 2.3 | 321.89 | 3.41 | 3.58 | 28.5 | 365.18 | 167.83 | 2467.851 | 309.83 | 291.34 | 4284 | 2.1 | 565.87 | 5.08 | 153.43 | 87.2599
893.8182 | 566.7672 | 14.1934 | 565.2449 | 94.7513 | 7.726 | 252.9946 | 884.8422 | 135.4612 | 3.775 | 563.3913 | 14.0701 | 565.2449 | 2.0433 | 11.1779 | 2.2767 | 15.6982 | -92.2328 | 37.744 | 2.28 | 324.05 | 3.37 | 3.72 | 28.5 | 368.29 | 167.03 | 2487.4214 | 306.3 | 287.67 | 4284 | 2.08 | 566.21 | 4.87 | 153.74 | 86.9602
865.6444 | 568.5054 | 13.8365 | 566.1675 | 97.9356 | 4.2666 | 251.3433 | 856.3392 | 133.9487 | 3.9017 | 564.5108 | 13.7188 | 566.1675 | 1.9806 | 10.8037 | 2.2078 | 15.273 | -92.3717 | 37.2491 | 2.21 | 325.02 | 3.49 | 3.8 | 28.5 | 367.53 | 162.27 | 2497.0893 | 296.6 | 278.39 | 4284 | 2.02 | 566.5 | 4.75 | 151.37 | 87.0899
861.7635 | 567.8681 | 13.7107 | 565.7084 | 112.5141 | 7.1015 | 251.1475 | 851.9179 | 134.4868 | 3.7861 | 564.1556 | 13.5899 | 565.7084 | 1.9719 | 10.7444 | 2.1983 | 15.1118 | -92.2992 | 37.5988 | 2.2 | 325.31 | 3.63 | 3.44 | 28 | 367.93 | 169.4 | 2629.1921 | 294.28 | 276.02 | 4284 | 2 | 566.36 | 4.67 | 151.37 | 83.122
927.3175 | 567.7285 | 14.8759 | 566.7832 | 106.7792 | 5.2757 | 254.9515 | 923.9127 | 137.3945 | 3.8089 | 564.1895 | 14.7455 | 566.7832 | 2.119 | 11.6153 | 2.3605 | 16.4113 | -92.2842 | 37.749 | 2.35 | 322.51 | 4.1 | 3.36 | 29 | 372.09 | 187.64 | 2688.7305 | 317.74 | 298.97 | 4284 | 2.15 | 566.7 | 5.14 | 154.81 | 79.7405
963.9971 | 567.4483 | 15.4476 | 566.3151 | 95.5395 | 7.0215 | 256.8215 | 957.1161 | 140.8776 | 3.7782 | 563.9488 | 15.3099 | 566.3151 | 2.2021 | 12.0383 | 2.4497 | 17.0728 | -92.5382 | 37.7563 | 2.44 | 322.01 | 3.9 | 3.32 | 29.5 | 375.38 | 192.44 | 2639.2194 | 331.55 | 312.37 | 4284 | 2.24 | 566.71 | 5.36 | 156.43 | 80.6633
937.2026 | 568.2395 | 15.1683 | 566.7734 | 86.5949 | 7.481 | 255.4391 | 930.7433 | 137.5171 | 3.7793 | 564.6361 | 15.0332 | 566.7734 | 2.1423 | 11.7033 | 2.3852 | 16.7649 | -92.8355 | 37.2693 | 2.38 | 322.42 | 3.59 | 3.38 | 29 | 372.63 | 185.51 | 2604.289 | 323.86 | 305.16 | 4284 | 2.18 | 567.04 | 5.28 | 155.74 | 81.6426
936.5517 | 568.2046 | 15.3522 | 565.7093 | 97.0844 | 4.2826 | 255.5518 | 933.2526 | 135.5919 | 3.5604 | 564.5332 | 15.2188 | 565.7093 | 2.1408 | 11.722 | 2.3834 | 16.9161 | -92.6498 | 37.7491 | 2.38 | 321.29 | 3.23 | 3.19 | 29 | 370.43 | 184.66 | 2602.2482 | 322.68 | 304 | 4284 | 2.18 | 566.29 | 5.32 | 154.89 | 81.7549
914.1186 | 568.0256 | 14.7311 | 565.916 | 89.1842 | 4.7125 | 254.2617 | 908.2815 | 135.0929 | 3.527 | 564.2755 | 14.6063 | 565.916 | 2.0815 | 11.4234 | 2.3285 | 16.2876 | -92.7031 | 37.7021 | 2.33 | 322.41 | 3.39 | 3.29 | 29 | 368.3 | 180.07 | 2599.6491 | 315.4 | 296.74 | 4284 | 2.13 | 565.95 | 5.14 | 153.95 | 82.1528
884.956 | 567.8806 | 14.107 | 565.9161 | 85.1005 | 4.4452 | 252.5446 | 885.0082 | 133.8098 | 3.6899 | 564.1573 | 13.9796 | 565.9161 | 2.0228 | 11.1426 | 2.2544 | 15.6529 | -92.5654 | 38.1197 | 2.24 | 323.81 | 3.02 | 3.41 | 30 | 368.52 | 170.52 | 2559.5924 | 303.72 | 285.4 | 4284 | 2.05 | 566.64 | 4.87 | 152.08 | 84.1041
870.8954 | 567.4403 | 14.0437 | 565.8212 | 98.3186 | 3.7828 | 251.8471 | 871.0607 | 136.2008 | 3.6395 | 563.9032 | 13.9239 | 565.8212 | 1.9921 | 10.9691 | 2.2211 | 15.507 | -92.7184 | 37.7418 | 2.22 | 323.36 | 3.07 | 3.59 | 29 | 367.87 | 167.71 | 2555.6491 | 300 | 281.13 | 4284 | 2.02 | 566.06 | 4.83 | 151.5 | 84.2271
912.482 | 568.0605 | 14.6875 | 566.4468 | 100.1649 | 6.5665 | 253.9754 | 907.1359 | 135.1277 | 3.6702 | 564.509 | 14.5566 | 566.4468 | 2.0872 | 11.4099 | 2.3239 | 16.1692 | -92.8142 | 37.4037 | 2.31 | 323.19 | 3.26 | 3.55 | 26 | 372.26 | 176.45 | 2568.5949 | 313.56 | 294.29 | 4284 | 2.11 | 566.91 | 5.05 | 154.34 | 83.8263
910.8732 | 567.6345 | 14.8269 | 566.24 | 105.1845 | 3.6822 | 254.0604 | 909.8654 | 133.6022 | 3.4711 | 564.1305 | 14.6981 | 566.24 | 2.0814 | 11.4223 | 2.3182 | 16.2994 | -92.7553 | 37.5163 | 2.31 | 322.21 | 3.58 | 3.44 | 28 | 369.76 | 179.48 | 2606.6797 | 313.89 | 294.97 | 4284 | 2.11 | 566.79 | 5.11 | 153.83 | 81.897
905.3866 | 568.2583 | 14.8082 | 566.4279 | 110.149 | 3.1819 | 253.8951 | 902.545 | 131.1817 | 3.6859 | 564.5493 | 14.6791 | 566.4279 | 2.0684 | 11.3244 | 2.3055 | 16.2383 | -92.9744 | 36.9289 | 2.3 | 322.3 | 3.78 | 3.63 | 28 | 368.38 | 184.22 | 2690.0632 | 312.36 | 293.17 | 4281 | 2.1 | 566.51 | 5.09 | 152.74 | 79.4364
872.1291 | 568.1858 | 14.2138 | 566.3617 | 107.2658 | 2.1074 | 252.1166 | 872.6029 | 128.3837 | 3.6076 | 564.5323 | 14.0849 | 566.3617 | 1.9952 | 10.9741 | 2.2247 | 15.5977 | -92.9049 | 37.2417 | 2.21 | 323.2 | 3.84 | 3.59 | 27 | 364.21 | 173.36 | 2636.9889 | 299.95 | 281.44 | 4281 | 2.02 | 566.36 | 4.83 | 148.01 | 81.4706
898.0649 | 567.963 | 14.6908 | 565.5768 | 109.1806 | 3.0643 | 253.5363 | 897.9389 | 130.4871 | 3.6527 | 564.4231 | 14.561 | 565.5768 | 2.0526 | 11.2714 | 2.2876 | 16.1337 | -92.6042 | 37.9862 | 2.27 | 322.39 | 3.88 | 3.63 | 28 | 366.32 | 180.63 | 2679.3148 | 307.58 | 288.61 | 4281 | 2.08 | 566.03 | 5.03 | 150.73 | 80.3057
899.9899 | 567.664 | 14.666 | 565.4372 | 75.7044 | 2.9914 | 253.6105 | 900.2108 | 132.318 | 3.5169 | 564.0007 | 14.5321 | 565.4372 | 2.0567 | 11.2954 | 2.2928 | 16.2234 | -92.7233 | 37.46 | 2.27 | 322.51 | 3.16 | 3.52 | 29 | 368.33 | 170.65 | 2532.2449 | 307.94 | 288.5 | 4281 | 2.08 | 565.85 | 5.05 | 151.66 | 85.1729
877.4576 | 567.911 | 14.1251 | 565.4345 | 79.0437 | 2.3249 | 252.3035 | 879.836 | 133.5423 | 3.6794 | 564.373 | 13.992 | 565.4345 | 2.0054 | 11.0553 | 2.2364 | 15.652 | -92.8408 | 37.6985 | 2.24 | 323.15 | 3.14 | 3.59 | 29.5 | 367.92 | 165.2 | 2482.6975 | 304.31 | 284.86 | 4281 | 2.05 | 566.09 | 4.91 | 151.11 | 85.9678
886.4005 | 567.7857 | 14.4286 | 566.1881 | 87.1355 | 1.9475 | 252.621 | 889.5802 | 131.9784 | 3.7177 | 564.2943 | 14.3026 | 566.1881 | 2.0267 | 11.1402 | 2.259 | 15.9391 | -92.7962 | 37.968 | 2.25 | 322.98 | 3.27 | 3.79 | 28 | 367.91 | 163.68 | 2455.6302 | 304.7 | 285.35 | 4281 | 2.05 | 566.31 | 4.96 | 150.88 | 87.5533
895.923 | 568.0928 | 14.5344 | 566.0816 | 82.4695 | 5.5667 | 253.0393 | 893.8904 | 129.4472 | 3.9465 | 564.6675 | 14.4088 | 566.0816 | 2.0479 | 11.1889 | 2.2819 | 16.0421 | -92.7593 | 38.0598 | 2.28 | 323.46 | 3.58 | 3.91 | 27 | 369.66 | 166.11 | 2463.7664 | 308.13 | 288.63 | 4281 | 2.08 | 566.31 | 5.01 | 152 | 87.4086
930.2654 | 568.2144 | 15.0383 | 566.2382 | 93.3494 | 6.6242 | 255.1703 | 930.5879 | 133.361 | 4.1389 | 564.535 | 14.9076 | 566.2382 | 2.1257 | 11.6602 | 2.3664 | 16.5701 | -92.6615 | 38.1748 | 2.36 | 322.15 | 3.55 | 3.93 | 29 | 370.97 | 173.92 | 2483.3284 | 319.72 | 299.82 | 4281 | 2.15 | 566.43 | 5.19 | 153.84 | 86.3205
936.406 | 567.8027 | 15.1006 | 565.8919 | 90.9106 | 8.6952 | 255.3163 | 934.5027 | 135.4871 | 4.2381 | 564.416 | 14.9609 | 565.8919 | 2.1399 | 11.7124 | 2.3817 | 16.6514 | -92.9969 | 37.2432 | 2.38 | 322.28 | 3.78 | 4.03 | 29.5 | 374.11 | 175.04 | 2468.1211 | 323.57 | 303.61 | 4281 | 2.18 | 566.44 | 5.23 | 155.79 | 86.4873
966.077 | 567.6578 | 15.66 | 566.3456 | 98.9098 | 9.1878 | 256.8443 | 962.6842 | 131.3543 | 4.1554 | 564.3838 | 15.5232 | 566.3456 | 2.2058 | 12.0345 | 2.4542 | 17.1921 | -92.9531 | 37.2656 | 2.44 | 321.96 | 3.76 | 3.97 | 28 | 372.03 | 179.22 | 2460.2091 | 332.01 | 311.86 | 4281 | 2.23 | 566.88 | 5.36 | 155.99 | 86.8865
964.4435 | 567.4859 | 15.5501 | 565.754 | 109.4433 | 8.9102 | 256.8898 | 961.3777 | 133.4697 | 4.2075 | 564.0714 | 15.4126 | 565.754 | 2.2021 | 12.031 | 2.4495 | 17.0807 | -92.5585 | 38.2413 | 2.43 | 321.54 | 4.22 | 4.09 | 28.5 | 371.69 | 183.54 | 2535.2007 | 330.2 | 309.93 | 4281 | 2.23 | 566.05 | 5.37 | 155.94 | 84.5122
910.8081 | 567.9146 | 14.7187 | 565.8543 | 109.0537 | 8.406 | 254.0342 | 911.8875 | 135.0605 | 4.1312 | 564.4858 | 14.5954 | 565.8543 | 2.0821 | 11.415 | 2.3193 | 16.1814 | -92.81 | 37.7252 | 2.32 | 322.74 | 4.55 | 4.03 | 29 | 369.96 | 177.34 | 2582.0241 | 314.14 | 294.03 | 4281 | 2.12 | 565.9 | 5.08 | 152.36 | 83.0587
958.0672 | 568.3479 | 15.4372 | 566.436 | 102.588 | 6.613 | 256.7318 | 960.9179 | 135.0815 | 4.3458 | 564.825 | 15.3011 | 566.436 | 2.1874 | 12.0305 | 2.434 | 16.9889 | -92.605 | 38.1451 | 2.44 | 321.35 | 4.42 | 4.3 | 28.5 | 372.55 | 181.4 | 2501.0415 | 331.87 | 310.5 | 4281 | 2.23 | 566.18 | 5.36 | 156.17 | 84.8836
960.7206 | 567.6389 | 15.5508 | 565.9563 | 105.8235 | 4.9473 | 256.8977 | 963.9092 | 134.5734 | 4.0179 | 564.2808 | 15.412 | 565.9563 | 2.1941 | 12.0563 | 2.4412 | 17.1182 | -92.6741 | 37.8892 | 2.43 | 320.83 | 3.65 | 4.05 | 29 | 368.48 | 180.94 | 2509.8961 | 330.24 | 308.62 | 4281 | 2.22 | 565.96 | 5.39 | 155.94 | 85.1709
988.2962 | 567.6094 | 15.7308 | 565.9366 | 90.8794 | 7.93 | 258.3765 | 983.0404 | 132.6077 | 4.2397 | 564.2728 | 15.5878 | 565.9366 | 2.2558 | 12.3191 | 2.5106 | 17.3776 | -92.7005 | 37.6883 | 2.5 | 321.59 | 3.57 | 4.06 | 29.5 | 371.83 | 187.99 | 2520.5462 | 340.51 | 319.29 | 4281 | 2.29 | 566.36 | 5.48 | 157.55 | 84.5488
971.886 | 568.014 | 15.5987 | 566.2445 | 84.8321 | 8.5208 | 256.9656 | 974.1221 | 131.2243 | 4.2718 | 564.6988 | 15.4561 | 566.2445 | 2.2188 | 12.1769 | 2.4692 | 17.2357 | -92.6888 | 37.7938 | 2.47 | 321.38 | 3.71 | 4.11 | 29.5 | 371.17 | 186.37 | 2528.2821 | 336.16 | 315.57 | 4281 | 2.26 | 566.62 | 5.42 | 156.47 | 83.92
931.3596 | 568.7417 | 14.8771 | 566.7099 | 92.4439 | 6.8708 | 254.7081 | 935.1206 | 132.7326 | 3.805 | 565.2769 | 14.7373 | 566.7099 | 2.1276 | 11.7438 | 2.3688 | 16.4556 | -93.0741 | 36.84 | 2.36 | 322.06 | 3.48 | 3.86 | 29.5 | 367.78 | 183.74 | 2592.8435 | 323.34 | 303.37 | 4281 | 2.16 | 566.69 | 5.18 | 154.6 | 81.8318
914.6053 | 567.5093 | 14.7426 | 565.2494 | 84.7187 | 5.6041 | 253.5028 | 913.673 | 134.2938 | 3.7933 | 564.2531 | 14.6139 | 565.2494 | 2.0882 | 11.433 | 2.3267 | 16.3022 | -92.96 | 37.1565 | 2.32 | 322.88 | 3.45 | 3.78 | 30 | 367.09 | 171.95 | 2487.7254 | 315.47 | 295.9 | 4281 | 2.12 | 565.49 | 5.11 | 152.8 | 85.9236
901.4096 | 568.1196 | 14.631 | 565.9223 | 85.4477 | 2.2028 | 252.7393 | 902.071 | 132.0241 | 3.8864 | 564.9503 | 14.5041 | 565.9223 | 2.0602 | 11.2974 | 2.2951 | 16.1724 | -92.8458 | 37.416 | 2.29 | 322.76 | 3.43 | 3.78 | 29 | 366.7 | 169.47 | 2494.0736 | 310.33 | 290.89 | 4281 | 2.09 | 566.24 | 5.07 | 151.58 | 86.0853
896.5832 | 568.0059 | 14.4922 | 565.8453 | 83.4274 | 1.5333 | 252.5496 | 898.153 | 130.4665 | 3.8508 | 564.7382 | 14.3627 | 565.8453 | 2.0492 | 11.246 | 2.284 | 16.0373 | -92.9688 | 37.1463 | 2.28 | 322.99 | 3.55 | 3.89 | 28 | 364.85 | 169.86 | 2511.729 | 309.59 | 289.51 | 4281 | 2.08 | 566.24 | 5.03 | 150.59 | 85.3385
961.3654 | 568.022 | 15.51 | 566.3322 | 92.7783 | 4.6279 | 256.15 | 956.4883 | 134.1459 | 3.9028 | 564.7525 | 15.3704 | 566.3322 | 2.1956 | 11.9925 | 2.4441 | 17.0865 | -92.3974 | 38.4725 | 2.44 | 321.95 | 3.55 | 4.05 | 28.5 | 370.25 | 180.02 | 2481.9349 | 330.09 | 310.51 | 4281 | 2.23 | 566.71 | 5.37 | 155.51 | 86.0781
947.4908 | 567.5011 | 15.2817 | 565.9885 | 107.2207 | 6.6457 | 255.298 | 946.4084 | 133.3049 | 3.9589 | 564.399 | 15.1462 | 565.9885 | 2.1631 | 11.8372 | 2.4095 | 16.8181 | -92.6159 | 37.968 | 2.4 | 322 | 3.54 | 4.16 | 27 | 370.26 | 180.07 | 2521.8518 | 325.1 | 305.68 | 4281 | 2.19 | 566.53 | 5.28 | 155.23 | 84.9185
939.3911 | 568.4042 | 15.0216 | 566.7878 | 100.9022 | 4.6602 | 254.8979 | 940.1048 | 138.6544 | 3.9065 | 564.9995 | 14.8877 | 566.7878 | 2.1458 | 11.7627 | 2.3897 | 16.5845 | -92.824 | 37.447 | 2.37 | 322.79 | 3.21 | 4.2 | 27 | 374.05 | 178.99 | 2529.9838 | 322.28 | 302.87 | 4281 | 2.17 | 566.75 | 5.18 | 154.62 | 84.7022
960.3983 | 568.0354 | 15.4935 | 566.2776 | 91.0453 | 7.8666 | 256.0473 | 959.0796 | 137.4632 | 3.9619 | 564.9225 | 15.356 | 566.2776 | 2.1936 | 12.0003 | 2.4414 | 17.0976 | -92.7604 | 37.5431 | 2.43 | 321.81 | 3.34 | 4.23 | 28 | 373.25 | 182.45 | 2502.9432 | 331.5 | 312.06 | 4281 | 2.23 | 566.88 | 5.37 | 156.42 | 84.8574
944.236 | 568.1419 | 15.1952 | 565.9877 | 86.3658 | 5.7548 | 255.2259 | 940.8588 | 137.0685 | 3.9768 | 564.9968 | 15.0544 | 565.9877 | 2.1576 | 11.8075 | 2.4013 | 16.7806 | -92.828 | 37.3748 | 2.39 | 322.45 | 3.57 | 4.23 | 30.5 | 372.71 | 178.41 | 2489.9694 | 325.93 | 306.74 | 4281 | 2.19 | 566.83 | 5.26 | 154.42 | 85.5227
896.67 | 568.4328 | 14.532 | 566.5765 | 93.2134 | 3.484 | 252.4613 | 895.7946 | 134.2804 | 3.8176 | 565.2957 | 14.4009 | 566.5765 | 2.0499 | 11.2256 | 2.2839 | 16.0157 | -93.0614 | 36.9051 | 2.27 | 323.32 | 3.81 | 3.98 | 29 | 367.91 | 171.52 | 2533.1256 | 308.75 | 289.87 | 4281 | 2.08 | 566.69 | 4.97 | 151.6 | 84.7391
975.6584 | 568.2547 | 15.6045 | 566.7555 | 103.8115 | 12.0446 | 256.7299 | 975.0023 | 135.3893 | 3.5746 | 565.1212 | 15.4562 | 566.7555 | 2.2285 | 12.1829 | 2.4787 | 17.2122 | -92.5129 | 38.081 | 2.47 | 322 | 3.26 | 3.68 | 28.5 | 371.98 | 191.61 | 2593.9424 | 335.42 | 316.23 | 4281 | 2.26 | 567.15 | 5.4 | 157.23 | 82.0817
943.117 | 568.5206 | 15.3688 | 566.8316 | 98.7207 | 7.3251 | 255.2282 | 943.6225 | 131.731 | 3.7112 | 565.3754 | 15.2344 | 566.8316 | 2.1542 | 11.8011 | 2.3982 | 16.9169 | -92.8664 | 37.2642 | 2.38 | 321.72 | 3.43 | 3.89 | 27.5 | 368.78 | 186.17 | 2612.7517 | 324.33 | 305.04 | 4281 | 2.18 | 567.12 | 5.29 | 155.77 | 81.7725
982.1029 | 568.4544 | 15.595 | 566.5148 | 96.7232 | 7.7461 | 256.9323 | 983.7529 | 133.9407 | 3.7168 | 565.1901 | 15.4489 | 566.5148 | 2.2409 | 12.2996 | 2.493 | 17.2457 | -92.6488 | 37.7187 | 2.48 | 322.14 | 3.44 | 3.73 | 29.5 | 371.29 | 190.18 | 2560.8976 | 337.6 | 317.92 | 4281 | 2.27 | 566.96 | 5.42 | 157.24 | 83.0255
928.8333 | 568.4776 | 15.046 | 567.0715 | 89.5853 | 4.6965 | 254.1604 | 927.3118 | 136.9769 | 3.766 | 565.2608 | 14.9113 | 567.0715 | 2.1214 | 11.5975 | 2.3623 | 16.6233 | -92.747 | 37.58 | 2.36 | 322.8 | 3.53 | 3.73 | 30 | 369.12 | 179.23 | 2553.8664 | 319.84 | 300.44 | 4281 | 2.16 | 567.03 | 5.22 | 154.74 | 83.7682
918.043 | 568.508 | 14.8895 | 566.377 | 93.6043 | 7.2633 | 253.5428 | 914.4429 | 134.7335 | 3.6823 | 565.2698 | 14.7546 | 566.377 | 2.0969 | 11.4584 | 2.3357 | 16.4304 | -92.8955 | 37.2547 | 2.33 | 322.85 | 3.24 | 3.63 | 30.5 | 368.8 | 176.63 | 2542.1181 | 316.36 | 297.45 | 4281 | 2.13 | 566.8 | 5.15 | 154.47 | 84.3918
919.1806 | 567.4197 | 14.805 | 566.4683 | 83.8928 | 3.9292 | 253.6086 | 918.8097 | 141.5087 | 3.8329 | 564.382 | 14.6685 | 566.4683 | 2.1002 | 11.495 | 2.3393 | 16.3946 | -92.804 | 37.4745 | 2.33 | 322.76 | 3.35 | 3.67 | 29.5 | 368.41 | 176.3 | 2537.2332 | 316.42 | 296.91 | 4273 | 2.13 | 566.55 | 5.15 | 153.99 | 84.4661
879.9654 | 568.2288 | 14.1785 | 566.3483 | 105.463 | 4.1436 | 251.4567 | 875.4174 | 141.543 | 3.6499 | 565.0416 | 14.0456 | 566.3483 | 2.0129 | 10.9936 | 2.2427 | 15.6331 | -93.0196 | 36.9715 | 2.24 | 324.52 | 3.31 | 3.48 | 28.5 | 365.32 | 170.9 | 2566.7136 | 303.47 | 284.51 | 4273 | 2.05 | 567.23 | 4.87 | 152.48 | 84.0526
907.3612 | 567.8323 | 14.5554 | 566.2266 | 88.4771 | 5.0633 | 252.9152 | 906.3981 | 134.5187 | 3.8245 | 564.8626 | 14.4225 | 566.2266 | 2.0736 | 11.3448 | 2.3097 | 16.1181 | -92.824 | 37.4022 | 2.32 | 323.71 | 3.34 | 3.64 | 28.5 | 365.4 | 175.57 | 2544.4669 | 313.94 | 294.84 | 4273 | 2.12 | 566.98 | 5.05 | 153.94 | 84.0077
923.046 | 568.5573 | 15.1273 | 566.402 | 85.4792 | 6.2118 | 253.9376 | 919.4777 | 136.3576 | 3.8355 | 565.3897 | 14.9954 | 566.402 | 2.1104 | 11.5152 | 2.3487 | 16.6735 | -92.4884 | 38.1756 | 2.35 | 322.4 | 3.48 | 3.67 | 29.5 | 366.92 | 177.81 | 2551.9166 | 317.18 | 297.73 | 4273 | 2.15 | 566.84 | 5.2 | 155.17 | 84.263
904.9247 | 568.3237 | 14.8003 | 566.6293 | 87.5353 | 4.3074 | 252.82 | 901.0687 | 135.0382 | 3.7878 | 565.1677 | 14.6696 | 566.6293 | 2.0684 | 11.3054 | 2.3046 | 16.3103 | -93.1385 | 36.8003 | 2.3 | 323.07 | 3.65 | 3.66 | 28 | 365.91 | 175.48 | 2564.4722 | 312.48 | 292.39 | 4273 | 2.1 | 566.94 | 5.06 | 153.02 | 83.8916
931.1395 | 568.0265 | 15.0571 | 566.6929 | 92.5396 | 6.3633 | 254.2204 | 928.6705 | 136.2963 | 3.7251 | 564.6558 | 14.9217 | 566.6929 | 2.1272 | 11.6149 | 2.3692 | 16.6025 | -92.9134 | 37.5908 | 2.36 | 322.91 | 3.41 | 3.87 | 29 | 370.62 | 177.84 | 2516.5927 | 321.35 | 301.96 | 4273 | 2.16 | 566.85 | 5.18 | 155.36 | 84.9352
950.3643 | 568.3245 | 15.3925 | 567.2254 | 105.9414 | 14.3236 | 255.1564 | 943.2325 | 138.1059 | 3.7885 | 565.2268 | 15.2571 | 567.2254 | 2.1711 | 11.7974 | 2.4155 | 16.9025 | -92.8895 | 37.6414 | 2.41 | 322.69 | 3.46 | 4.03 | 29 | 372.87 | 180.93 | 2506.123 | 328.33 | 308.49 | 4273 | 2.21 | 567.14 | 5.3 | 156.98 | 85.4645
926.3845 | 567.8368 | 14.9522 | 565.8248 | 95.7465 | 10.507 | 254.0407 | 921.6666 | 136.9075 | 3.7514 | 564.6657 | 14.8241 | 565.8248 | 2.1173 | 11.5235 | 2.3573 | 16.4668 | -92.8477 | 37.8444 | 2.35 | 323.51 | 4.02 | 4.04 | 26.5 | 370.45 | 175.19 | 2508.9214 | 317.91 | 298.37 | 4273 | 2.15 | 566.96 | 5.12 | 154.95 | 85.9642
920.312 | 568.4588 | 14.6267 | 566.7349 | 96.4011 | 12.4118 | 253.4226 | 913.256 | 137.9243 | 3.7956 | 565.0935 | 14.4949 | 566.7349 | 2.1046 | 11.4514 | 2.343 | 16.1543 | -92.712 | 38.19 | 2.32 | 324.22 | 4 | 3.98 | 28.5 | 370.28 | 173.4 | 2514.3824 | 314.27 | 294.68 | 4273 | 2.12 | 567.15 | 5.01 | 154.45 | 86.5783
914.9339 | 568.3603 | 14.6443 | 566.8567 | 93.2768 | 12.0488 | 253.2351 | 907.4546 | 135.2666 | 3.7991 | 565.2438 | 14.5159 | 566.8567 | 2.0915 | 11.3774 | 2.3289 | 16.1539 | -92.8935 | 37.7209 | 2.32 | 323.89 | 4.06 | 4.11 | 27.5 | 369.66 | 169.48 | 2461.4664 | 313.81 | 294.21 | 4273 | 2.12 | 566.94 | 5.02 | 153.79 | 88.0521
889.1624 | 567.6461 | 14.3661 | 565.1133 | 79.5066 | 5.0781 | 251.9573 | 886.3914 | 134.9368 | 3.8229 | 564.5117 | 14.2395 | 565.1133 | 2.0333 | 11.1108 | 2.2654 | 15.8929 | -93.0312 | 37.3908 | 2.27 | 323.76 | 3.59 | 3.83 | 28.5 | 367.93 | 163.5 | 2426.4917 | 307.38 | 287.92 | 4273 | 2.07 | 565.94 | 4.94 | 152.58 | 88.5244
882.2871 | 568.4489 | 14.2285 | 566.3823 | 90.2857 | 6.6862 | 251.4221 | 877.6947 | 131.955 | 3.9777 | 565.1158 | 14.1075 | 566.3823 | 2.0185 | 10.9786 | 2.249 | 15.7178 | -93.1183 | 37.1935 | 2.25 | 324.37 | 3.53 | 3.98 | 27 | 370.39 | 166.01 | 2486.7164 | 304.64 | 285.26 | 4273 | 2.05 | 567.15 | 4.88 | 153.3 | 86.8784
883.7161 | 567.9746 | 14.3685 | 566.4638 | 101.215 | 9.5564 | 251.4839 | 876.5117 | 134.732 | 3.7987 | 564.799 | 14.246 | 566.4638 | 2.0214 | 10.9835 | 2.2528 | 15.8046 | -93.2892 | 36.723 | 2.24 | 324.28 | 3.65 | 3.68 | 28 | 367.56 | 168.92 | 2533.8593 | 304.18 | 284.86 | 4273 | 2.05 | 567.39 | 4.87 | 153.43 | 85.6288
895.0303 | 568.0757 | 14.3908 | 566.5685 | 104.1001 | 8.0239 | 252.2955 | 891.001 | 136.1855 | 3.7008 | 564.9449 | 14.2655 | 566.5685 | 2.0465 | 11.1614 | 2.2803 | 15.8518 | -92.9605 | 37.5727 | 2.27 | 324.01 | 3.43 | 3.48 | 28 | 365.55 | 170.41 | 2529.1304 | 307.28 | 287.91 | 4273 | 2.07 | 567.09 | 4.92 | 153.66 | 85.6985
894.7358 | 567.9979 | 14.4404 | 565.8928 | 100.728 | 8.9275 | 252.3449 | 888.6058 | 134.5087 | 3.7833 | 564.6406 | 14.3169 | 565.8928 | 2.0471 | 11.1341 | 2.2802 | 15.9136 | -92.8844 | 37.7765 | 2.28 | 323.69 | 3.59 | 3.6 | 28 | 367.34 | 172.3 | 2546.0383 | 308.75 | 289.17 | 4273 | 2.09 | 566.55 | 4.95 | 154.22 | 84.8659
881.351 | 567.8439 | 14.1766 | 565.533 | 86.8664 | 5.5097 | 251.4707 | 879.1827 | 132.4371 | 3.8053 | 564.5932 | 14.0481 | 565.533 | 2.0143 | 11.0295 | 2.2464 | 15.6816 | -92.9692 | 37.5907 | 2.25 | 323.68 | 4.04 | 3.75 | 28.5 | 365.58 | 167.56 | 2516.0202 | 304.04 | 284.57 | 4273 | 2.05 | 566.48 | 4.89 | 150.62 | 85.6626
939.5151 | 567.9594 | 15.2891 | 566.9112 | 92.6374 | 5.3244 | 254.7726 | 939.2466 | 136.4021 | 3.5634 | 565.1248 | 15.1598 | 566.9112 | 2.1459 | 11.7415 | 2.3897 | 16.8472 | -92.5974 | 38.4457 | 2.38 | 322.08 | 4.09 | 3.66 | 28.5 | 369.15 | 183.56 | 2585.122 | 322.97 | 303.41 | 4273 | 2.18 | 567.26 | 5.26 | 154.87 | 82.7759
934.7631 | 568.3523 | 15.2113 | 566.0798 | 100.3642 | 6.3144 | 254.6424 | 931.1176 | 136.3979 | 3.7091 | 565.3092 | 15.0791 | 566.0798 | 2.1349 | 11.6687 | 2.3778 | 16.7412 | -93.0507 | 37.1955 | 2.38 | 322.31 | 4.28 | 3.71 | 27 | 369.94 | 185.24 | 2602.4347 | 323.71 | 304.15 | 4273 | 2.18 | 567.08 | 5.26 | 155.23 | 81.7502
943.6254 | 568.2341 | 15.3597 | 566.7707 | 105.1245 | 4.2129 | 255.1799 | 942.0305 | 133.9829 | 3.7218 | 565.2071 | 15.2272 | 566.7707 | 2.1562 | 11.7933 | 2.4006 | 16.8859 | -92.8669 | 37.6378 | 2.4 | 321.88 | 4.3 | 3.62 | 27.5 | 366.29 | 182.71 | 2541.6539 | 327.08 | 307.17 | 4273 | 2.2 | 567.23 | 5.31 | 155.22 | 83.4707
971.0274 | 568.1724 | 15.6028 | 566.8531 | 118.8962 | 5.7586 | 256.6919 | 971.9194 | 132.8821 | 3.6399 | 565.2913 | 15.4632 | 566.8531 | 2.2176 | 12.1243 | 2.4681 | 17.1523 | -92.6009 | 38.3547 | 2.46 | 322 | 4.27 | 3.65 | 28 | 367.47 | 184.95 | 2517.8137 | 333.96 | 313.88 | 4273 | 2.25 | 567.29 | 5.4 | 156.65 | 84.5206
949.0004 | 568.0462 | 15.3881 | 566.6687 | 104.5793 | 3.3911 | 255.4111 | 952.4732 | 130.8092 | 3.7184 | 565.1132 | 15.251 | 566.6687 | 2.1669 | 11.8833 | 2.4123 | 16.943 | -92.8652 | 37.6602 | 2.41 | 321.72 | 4.36 | 3.69 | 29 | 365.17 | 181.37 | 2511.078 | 328.31 | 308.63 | 4273 | 2.21 | 567.32 | 5.33 | 155.07 | 84.2738
963.8855 | 568.0131 | 15.6354 | 566.3429 | 85.5213 | 5.6068 | 256.3131 | 966.0301 | 130.1947 | 3.7017 | 565.149 | 15.4991 | 566.3429 | 2.2007 | 12.0496 | 2.4505 | 17.2553 | -92.7323 | 37.9644 | 2.45 | 321.4 | 3.92 | 3.77 | 27.5 | 368.4 | 180.58 | 2464.6831 | 332.95 | 313.07 | 4273 | 2.24 | 566.69 | 5.42 | 155.76 | 85.9078
888.1147 | 568.4615 | 14.3281 | 566.1738 | 87.8745 | 2.9573 | 251.8062 | 886.5265 | 129.2617 | 3.7175 | 565.3306 | 14.2023 | 566.1738 | 2.03 | 11.1048 | 2.2625 | 15.822 | -92.9811 | 37.4044 | 2.26 | 323.94 | 3.61 | 3.79 | 27.5 | 364.16 | 165.16 | 2466.2893 | 305.48 | 286.15 | 4273 | 2.06 | 566.77 | 4.92 | 152.59 | 87.5254
862.4145 | 567.9335 | 13.8311 | 566.0646 | 93.7177 | 3.0064 | 250.4606 | 860.9 | 129.163 | 3.7629 | 564.8125 | 13.7058 | 566.0646 | 1.9728 | 10.7868 | 2.2003 | 15.2718 | -92.8786 | 37.7006 | 2.2 | 324.59 | 3.63 | 3.63 | 28.5 | 362.21 | 163.85 | 2519.4539 | 296.73 | 277.89 | 4273 | 2 | 566.72 | 4.73 | 151.08 | 85.8468
911.6791 | 568.3666 | 14.7967 | 566.0109 | 90.6834 | 3.9632 | 253.1893 | 911.4009 | 129.2062 | 3.6039 | 565.1821 | 14.6649 | 566.0109 | 2.0837 | 11.411 | 2.3212 | 16.3166 | -92.76 | 37.9015 | 2.31 | 322.82 | 3.37 | 3.68 | 28.5 | 364.12 | 170.49 | 2480.9419 | 312.66 | 293.64 | 4273 | 2.11 | 566.8 | 5.07 | 153.47 | 86.7274
886.8127 | 568.1626 | 14.3492 | 565.8928 | 83.3636 | 3.1452 | 251.7903 | 884.7889 | 130.3094 | 3.6883 | 564.8796 | 14.2221 | 565.8928 | 2.0276 | 11.0974 | 2.2606 | 15.8529 | -93.1775 | 36.7975 | 2.25 | 323.68 | 3.61 | 3.94 | 29.5 | 366.88 | 163.47 | 2429.1682 | 306.31 | 287.55 | 4273 | 2.06 | 566.6 | 4.93 | 150.95 | 88.1986
898.2323 | 568.1053 | 14.5826 | 566.0825 | 80.708 | 3.4094 | 252.3773 | 900.8758 | 129.8538 | 3.5706 | 564.9073 | 14.4559 | 566.0825 | 2.053 | 11.2616 | 2.2879 | 16.0913 | -93.0222 | 37.2779 | 2.29 | 323 | 3.69 | 3.91 | 29 | 365.7 | 165.22 | 2418.0883 | 310.89 | 291.96 | 4273 | 2.09 | 566.99 | 5.03 | 152.61 | 88.1706
876.94 | 567.7607 | 14.2049 | 566.5175 | 90.7538 | 6.2195 | 251.1613 | 874.8486 | 127.5625 | 3.7782 | 564.6872 | 14.0756 | 566.5175 | 2.0069 | 10.9457 | 2.2355 | 15.6536 | -92.9471 | 37.5127 | 2.24 | 323.4 | 4 | 4.07 | 30 | 362.49 | 161.14 | 2424.6469 | 303.16 | 283.98 | 4273 | 2.04 | 566.93 | 4.9 | 151.14 | 88.6271
870.6722 | 568.0713 | 14.1964 | 565.4873 | 78.4499 | 2.159 | 250.9101 | 869.6132 | 124.1042 | 3.8137 | 564.6263 | 14.0706 | 565.4873 | 1.9914 | 10.9028 | 2.2209 | 15.6671 | -93.0434 | 37.2743 | 2.22 | 323.66 | 4.38 | 4.11 | 29 | 361.14 | 161.79 | 2455.7 | 300.65 | 281.52 | 4273 | 2.03 | 566.59 | 4.88 | 149.72 | 87.5914
899.2645 | 568.3192 | 14.4059 | 565.0434 | 86.9625 | 4.247 | 252.5381 | 902.0476 | 123.4937 | 3.7386 | 564.7847 | 14.2661 | 565.0434 | 2.0553 | 11.2833 | 2.2913 | 15.9202 | -92.8926 | 37.6825 | 2.29 | 323.83 | 4.18 | 3.97 | 28 | 360.95 | 168.34 | 2479.3769 | 309.55 | 290.12 | 4273 | 2.09 | 566.25 | 4.96 | 150.26 | 86.6107
1171.5269 | 566.8657 | 17.4374 | 565.5876 | 92.053 | 24.208 | 266.3249 | 1163.0563 | 130.7552 | 3.6829 | 563.9318 | 17.2357 | 565.5876 | 2.6685 | 14.5097 | 2.961 | 19.4373 | -92.608 | 37.9082 | 2.94 | 321.57 | 3.78 | 4.06 | 28.5 | 380.61 | 215.24 | 2407.5646 | 404.44 | 380.94 | 4261 | 2.71 | 567.15 | 6.18 | 164.4 | 87.0178
1178.4549 | 567.3588 | 17.5935 | 565.465 | 89.6294 | 31.9057 | 266.5273 | 1167.8683 | 130.3495 | 3.5004 | 564.1341 | 17.3968 | 565.465 | 2.6846 | 14.4976 | 2.9776 | 19.5786 | -92.6802 | 37.7361 | 2.96 | 321.85 | 3.11 | 4.1 | 27.5 | 382.74 | 213.16 | 2374.2021 | 405.79 | 382.56 | 4261 | 2.73 | 566.16 | 6.19 | 164.79 | 88.6355
1154.2828 | 568.1303 | 17.2495 | 566.419 | 108.6488 | 33.2699 | 265.236 | 1139.7825 | 130.9771 | 3.328 | 564.4142 | 17.0541 | 566.419 | 2.6311 | 14.1585 | 2.9188 | 19.1205 | -92.3891 | 38.4335 | 2.91 | 322.24 | 2.93 | 4.12 | 28.5 | 381.88 | 211.33 | 2405.0563 | 396.86 | 374.41 | 4261 | 2.68 | 566.71 | 6.05 | 164.36 | 87.9425
990.8938 | 567.6685 | 15.8507 | 565.8292 | 102.99 | 12.2679 | 257.6 | 982.796 | 127.2591 | 3.6407 | 564.0705 | 15.7028 | 565.8292 | 2.2631 | 12.2251 | 2.5168 | 17.409 | -93.0795 | 36.9513 | 2.51 | 322.15 | 3.12 | 3.86 | 26.5 | 368.5 | 185.26 | 2459.1678 | 341.95 | 321 | 4261 | 2.3 | 566.65 | 5.47 | 157.7 | 86.7368
1023.9312 | 567.3999 | 16.0352 | 564.954 | 101.6081 | 15.5818 | 259.0295 | 1018.9325 | 127.3737 | 3.6237 | 563.8933 | 15.8757 | 564.954 | 2.3366 | 12.6458 | 2.5975 | 17.678 | -92.855 | 37.5426 | 2.6 | 322.3 | 3.17 | 3.87 | 28 | 370.77 | 187.82 | 2410.7631 | 353.63 | 331.97 | 4261 | 2.38 | 566.32 | 5.57 | 158.64 | 88.1509
991.5417 | 567.9916 | 15.9073 | 566.2588 | 102.1638 | 14.2846 | 257.473 | 987.1238 | 125.3057 | 3.654 | 564.3972 | 15.7494 | 566.2588 | 2.2634 | 12.2368 | 2.5174 | 17.4699 | -92.6804 | 38.1278 | 2.51 | 321.89 | 3.54 | 3.86 | 26.5 | 366.89 | 180.09 | 2401.5382 | 340.43 | 319.53 | 4261 | 2.3 | 566.8 | 5.49 | 157.37 | 89.1994
902.1287 | 568.0605 | 14.5726 | 565.9707 | 85.8577 | 3.3338 | 252.6541 | 901.6676 | 123.1301 | 3.6944 | 564.0374 | 14.4432 | 565.9707 | 2.0637 | 11.2288 | 2.2994 | 16.0522 | -93.0959 | 37.0734 | 2.31 | 322.83 | 3.91 | 3.9 | 27.5 | 362.17 | 167.4 | 2427.9781 | 313.89 | 293.78 | 4261 | 2.11 | 565.81 | 5.06 | 152.42 | 87.6447
1102.8731 | 567.0429 | 16.6641 | 565.524 | 96.1402 | 20.1985 | 262.8152 | 1100.1837 | 126.9359 | 3.3819 | 563.4342 | 16.4849 | 565.524 | 2.5144 | 13.642 | 2.7912 | 18.4898 | -92.5 | 38.2912 | 2.78 | 321.84 | 3.36 | 3.48 | 28 | 370.67 | 201.09 | 2390.8826 | 380.38 | 358.38 | 4261 | 2.56 | 566.78 | 5.86 | 161.78 | 88.0381
1008.888 | 567.818 | 15.9819 | 565.6198 | 99.7882 | 12.333 | 258.3665 | 1004.9606 | 124.5347 | 3.5513 | 564.1475 | 15.8305 | 565.6198 | 2.3028 | 12.4851 | 2.5613 | 17.5772 | -92.7813 | 37.648 | 2.56 | 321.69 | 3.92 | 3.46 | 26 | 361.87 | 184.29 | 2395.8375 | 348.53 | 327.76 | 4261 | 2.35 | 566.8 | 5.55 | 157.83 | 88.4628
985.3142 | 568.193 | 15.5855 | 565.7111 | 97.7222 | 12.1599 | 257.1325 | 977.8537 | 124.537 | 3.5656 | 564.1054 | 15.436 | 565.7111 | 2.2505 | 12.1839 | 2.5039 | 17.1576 | -92.7747 | 37.7664 | 2.5 | 322.2 | 4.04 | 3.61 | 26.5 | 361.52 | 184.8 | 2467.7452 | 339.93 | 319.09 | 4261 | 2.29 | 566.51 | 5.4 | 155.92 | 86.3765
972.3603 | 567.9764 | 15.4288 | 566.1084 | 90.3379 | 6.1365 | 256.4179 | 969.0502 | 125.7029 | 3.6922 | 564.024 | 15.279 | 566.1084 | 2.2197 | 12.0944 | 2.471 | 17.0673 | -92.7485 | 37.9254 | 2.47 | 322.3 | 4 | 3.88 | 27.5 | 366.28 | 184.72 | 2500.9276 | 335.59 | 314.72 | 4261 | 2.26 | 566.27 | 5.35 | 154.78 | 85.1341
988.0885 | 568.2987 | 15.7051 | 565.372 | 86.9843 | 7.6462 | 257.1772 | 989.3352 | 123.8534 | 3.4855 | 564.442 | 15.5511 | 565.372 | 2.2538 | 12.3008 | 2.5089 | 17.3727 | -92.8956 | 37.4413 | 2.51 | 321.77 | 3.22 | 3.63 | 26.5 | 365.44 | 187.84 | 2494.5808 | 342.09 | 320.85 | 4261 | 2.3 | 566.03 | 5.48 | 156.11 | 84.8424
991.0023 | 567.5405 | 15.6975 | 565.4677 | 74.1553 | 10.3436 | 257.3385 | 987.7425 | 124.3687 | 3.5346 | 563.7 | 15.5491 | 565.4677 | 2.2621 | 12.2914 | 2.5168 | 17.3818 | -92.7589 | 37.7809 | 2.5 | 322.18 | 3.74 | 3.85 | 27 | 365.52 | 182.9 | 2443.139 | 340 | 318.99 | 4261 | 2.29 | 566.71 | 5.45 | 156.82 | 87.5986
891.2702 | 567.9343 | 14.2985 | 565.1885 | 84.2231 | 4.0174 | 251.9495 | 894.531 | 124.3303 | 3.5991 | 563.922 | 14.164 | 565.1885 | 2.038 | 11.1305 | 2.2708 | 15.8191 | -92.8753 | 37.6443 | 2.28 | 323.38 | 3.67 | 3.7 | 27.5 | 359.43 | 166.12 | 2463.3281 | 307.71 | 287.35 | 4261 | 2.08 | 565.78 | 4.93 | 151.51 | 87.311
942.1313 | 567.2568 | 15.0481 | 565.6949 | 84.1637 | 4.3274 | 254.8996 | 941.2269 | 125.8007 | 3.6702 | 563.5067 | 14.9069 | 565.6949 | 2.1528 | 11.7378 | 2.3966 | 16.6317 | -93.0322 | 37.1088 | 2.4 | 322.45 | 4.04 | 3.61 | 27.5 | 360.93 | 170.72 | 2382.7768 | 326.03 | 305.29 | 4261 | 2.19 | 566.48 | 5.22 | 154.73 | 89.3412
883.6386 | 566.966 | 14.1485 | 564.4394 | 82.0406 | 3.6753 | 251.6013 | 884.3532 | 125.982 | 3.6502 | 563.1881 | 14.0114 | 564.4394 | 2.0197 | 11.0365 | 2.2519 | 15.6399 | -92.97 | 37.3516 | 2.24 | 323.54 | 4.23 | 3.81 | 28 | 359.43 | 158.77 | 2392.3016 | 302.83 | 282.79 | 4261 | 2.04 | 564.85 | 4.83 | 149.9 | 90.4547
945.0389 | 567.9254 | 15.2997 | 565.7621 | 84.036 | 5.5102 | 255.2602 | 944.3725 | 123.1283 | 3.5522 | 563.7904 | 15.1611 | 565.7621 | 2.1575 | 11.7733 | 2.4034 | 16.8638 | -92.6769 | 37.9904 | 2.39 | 321.73 | 3.98 | 3.79 | 28 | 360.67 | 167.87 | 2357.7496 | 323.94 | 303.38 | 4261 | 2.19 | 566.18 | 5.26 | 153.26 | 91.0388
1000.8007 | 567.1933 | 15.8699 | 564.7991 | 84.41 | 5.6376 | 258.7018 | 998.6893 | 127.4336 | 3.564 | 563.1828 | 15.7145 | 564.7991 | 2.2844 | 12.4725 | 2.5414 | 17.5592 | -92.5772 | 38.1147 | 2.52 | 321.41 | 4.08 | 3.7 | 28 | 367.9 | 180.85 | 2398.0142 | 342.53 | 321.35 | 4261 | 2.31 | 565.51 | 5.49 | 156.63 | 88.8551
988.1598 | 568.2038 | 15.7802 | 564.8 | 83.5668 | 5.5078 | 257.9386 | 988.1348 | 128.0594 | 3.7084 | 563.7376 | 15.6289 | 564.8 | 2.2545 | 12.3199 | 2.5092 | 17.4413 | -92.6429 | 37.9095 | 2.51 | 321.36 | 4.75 | 3.76 | 27.5 | 367.82 | 186.99 | 2485.384 | 341.69 | 320.58 | 4261 | 2.3 | 566 | 5.51 | 156.19 | 85.0294
960.7547 | 567.9406 | 15.3212 | 564.8743 | 75.4261 | 5.2 | 256.4094 | 961.4778 | 124.5757 | 3.6376 | 563.411 | 15.1696 | 564.8743 | 2.1934 | 11.99 | 2.4418 | 16.9597 | -92.8438 | 37.4058 | 2.43 | 321.86 | 4.51 | 3.77 | 29 | 363.3 | 175.42 | 2412.7328 | 330.95 | 309.8 | 4261 | 2.23 | 565.55 | 5.34 | 152.57 | 88.3623
881.9368 | 567.5494 | 14.1005 | 564.9101 | 76.2203 | 1.7416 | 252.1755 | 885.8145 | 122.6203 | 3.5279 | 563.189 | 13.9675 | 564.9101 | 2.0158 | 11.0327 | 2.2481 | 15.6185 | -92.776 | 37.7325 | 2.24 | 323.8 | 3.96 | 3.75 | 27 | 359.7 | 161 | 2426.9325 | 302.79 | 282.67 | 4261 | 2.04 | 565.49 | 4.85 | 149.12 | 88.8298
935.1103 | 568.065 | 14.831 | 565.6306 | 90.7376 | 7.177 | 255.0315 | 930.4163 | 125.0159 | 3.6845 | 563.6982 | 14.688 | 565.6306 | 2.1362 | 11.6403 | 2.379 | 16.3823 | -92.6374 | 37.9775 | 2.36 | 323.28 | 3.61 | 3.94 | 28 | 363.49 | 172.5 | 2456.1335 | 320.06 | 299.26 | 4261 | 2.16 | 566.08 | 5.1 | 152.18 | 87.9474
1041.7611 | 567.1843 | 16.3065 | 565.9742 | 103.2826 | 6.9685 | 260.8592 | 1045.0421 | 126.9466 | 3.4224 | 563.1774 | 16.1408 | 565.9742 | 2.3774 | 12.9869 | 2.6413 | 18.0171 | -92.6165 | 37.8322 | 2.63 | 321 | 3.4 | 3.82 | 28.5 | 366.65 | 190.22 | 2394.751 | 360.04 | 338.46 | 4261 | 2.42 | 566.52 | 5.72 | 159.44 | 87.5341
1006.619 | 567.3624 | 16.2018 | 565.541 | 107.2544 | 6.2431 | 259.1275 | 1009.2423 | 125.5523 | 3.4576 | 563.2024 | 16.0483 | 565.541 | 2.2973 | 12.5385 | 2.5554 | 17.7735 | -92.4884 | 38.2282 | 2.55 | 320.64 | 3.78 | 3.62 | 28.5 | 360.46 | 184.13 | 2411.2666 | 346.55 | 325.38 | 4261 | 2.34 | 566.42 | 5.61 | 158.19 | 87.6468
943.9261 | 567.792 | 15.2375 | 566.5747 | 107.9036 | 7.8264 | 255.7611 | 940.8512 | 125.9452 | 3.531 | 563.5327 | 15.0949 | 566.5747 | 2.1569 | 11.7464 | 2.4009 | 16.684 | -92.6916 | 37.8155 | 2.4 | 321.92 | 3.79 | 3.68 | 28 | 356.89 | 176.68 | 2470.0882 | 325.39 | 304.78 | 4261 | 2.2 | 566.45 | 5.24 | 155.03 | 86.3737
1017.8309 | 567.0563 | 15.8476 | 565.7424 | 90.594 | 4.5711 | 259.6784 | 1021.7828 | 126.3836 | 3.4898 | 563.1255 | 15.6824 | 565.7424 | 2.3224 | 12.7259 | 2.5822 | 17.565 | -92.5771 | 38.0222 | 2.56 | 321.82 | 2.94 | 3.57 | 26 | 364.61 | 195.82 | 2551.7264 | 348.31 | 326.99 | 4261 | 2.34 | 567 | 5.51 | 157.46 | 83.224
998.3023 | 567.8681 | 15.9193 | 565.9187 | 95.6203 | 2.6455 | 258.9215 | 1002.0045 | 125.6806 | 3.4771 | 563.6553 | 15.7635 | 565.9187 | 2.2775 | 12.4431 | 2.5348 | 17.5681 | -92.4403 | 38.3995 | 2.53 | 320.96 | 3.62 | 3.7 | 28 | 361.9 | 191.83 | 2527.3256 | 344.36 | 323.42 | 4261 | 2.32 | 566.12 | 5.54 | 156.27 | 83.3027
931.1705 | 567.8278 | 14.8874 | 565.4739 | 93.1022 | 4.9178 | 255.0771 | 931.1704 | 122.9647 | 3.5663 | 563.6624 | 14.7463 | 565.4739 | 2.1272 | 11.6008 | 2.3691 | 16.4111 | -92.9326 | 37.267 | 2.36 | 322.8 | 3.75 | 3.84 | 27 | 360.32 | 180.85 | 2570.9867 | 320.24 | 299.73 | 4261 | 2.16 | 565.84 | 5.13 | 152.31 | 83.2686
1033.7792 | 567.7123 | 16.2264 | 565.8462 | 73.0562 | 8.1097 | 260.6629 | 1032.1997 | 126.5225 | 3.2627 | 563.8074 | 16.0652 | 565.8462 | 2.357 | 12.8731 | 2.6213 | 17.9929 | -92.3958 | 38.4371 | 2.61 | 321.1 | 3.39 | 3.68 | 27.5 | 366.39 | 194.19 | 2475.0788 | 355.79 | 334.31 | 4261 | 2.4 | 566.53 | 5.69 | 158.82 | 85.3014
1007.2637 | 568.0471 | 16.1586 | 566.3993 | 85.2632 | 9.2567 | 259.3907 | 1007.5273 | 125.79 | 3.5178 | 564.3122 | 16.0087 | 566.3993 | 2.2989 | 12.487 | 2.5554 | 17.8349 | -92.3728 | 38.5368 | 2.55 | 320.87 | 3.43 | 4.04 | 27 | 366.5 | 188.24 | 2470.1754 | 345.99 | 324.71 | 4261 | 2.34 | 566.58 | 5.64 | 157.7 | 86.0177
957.9494 | 567.9272 | 15.3628 | 565.8302 | 91.0227 | 3.6407 | 256.7214 | 958.8706 | 124.4349 | 3.4177 | 564.2021 | 15.2165 | 565.8302 | 2.1876 | 11.9641 | 2.4356 | 16.9413 | -92.8373 | 37.3913 | 2.43 | 321.83 | 3.12 | 3.79 | 27.5 | 362.77 | 175.01 | 2412.6229 | 329.82 | 309.09 | 4261 | 2.22 | 566.27 | 5.33 | 155.12 | 88.2352
899.5869 | 568.0749 | 14.4688 | 565.7612 | 87.0794 | 3.3544 | 253.4098 | 898.6361 | 125.1876 | 3.6386 | 564.2245 | 14.3364 | 565.7612 | 2.0559 | 11.263 | 2.2911 | 15.9856 | -92.7586 | 37.7151 | 2.29 | 323.03 | 3.42 | 3.89 | 27 | 362.19 | 169.75 | 2486.9043 | 309.29 | 289.23 | 4237.3333 | 2.09 | 565.61 | 4.99 | 151.38 | 86.5418
880.3931 | 567.7204 | 14.1277 | 566.3761 | 104.9067 | 2.8773 | 252.4201 | 881.2982 | 126.9419 | 3.5013 | 563.7824 | 13.9981 | 566.3761 | 2.0141 | 11.006 | 2.2448 | 15.5572 | -92.8218 | 37.616 | 2.24 | 323.85 | 3.4 | 3.66 | 25.5 | 357.36 | 171.27 | 2575.1475 | 301.91 | 281.82 | 4237.3333 | 2.04 | 566.61 | 4.83 | 150.89 | 84.1676
900.3526 | 567.4609 | 14.188 | 566.1398 | 93.65 | 5.3607 | 253.4329 | 898.3799 | 127.3443 | 3.5525 | 563.7323 | 14.0506 | 566.1398 | 2.0581 | 11.2472 | 2.2927 | 15.6899 | -92.8123 | 37.6045 | 2.29 | 324.45 | 3.77 | 4.04 | 26 | 362.08 | 176.65 | 2594.8103 | 308.88 | 288.47 | 4237.3333 | 2.09 | 566.47 | 4.89 | 151.9 | 83.4304
932.5871 | 567.0948 | 14.6061 | 565.3155 | 82.9719 | 6.7059 | 254.8921 | 932.108 | 126.6471 | 3.3917 | 563.3304 | 14.4553 | 565.3155 | 2.1304 | 11.651 | 2.3722 | 16.2034 | -92.6647 | 37.8979 | 2.36 | 323.22 | 3.25 | 3.75 | 27.5 | 365.34 | 172.63 | 2459.0408 | 318.28 | 297.47 | 4237.3333 | 2.15 | 565.48 | 5.04 | 151.63 | 88.0385
1019.2257 | 567.9227 | 15.8441 | 565.8042 | 94.3707 | 12.1016 | 259.6671 | 1017.635 | 127.6879 | 3.3388 | 563.8441 | 15.6807 | 565.8042 | 2.3254 | 12.7045 | 2.5849 | 17.5506 | -92.853 | 37.4254 | 2.57 | 322.4 | 3.07 | 3.66 | 28 | 366.93 | 187.54 | 2424.251 | 350.47 | 327.8 | 4237.3333 | 2.36 | 566.02 | 5.52 | 157.49 | 87.9245
1134.9155 | 567.2845 | 17.0545 | 565.6019 | 109.0236 | 24.8396 | 265.4973 | 1134.4551 | 129.7798 | 3.2276 | 563.3912 | 16.8616 | 565.6019 | 2.5867 | 14.0389 | 2.8702 | 18.9207 | -92.4213 | 38.6214 | 2.84 | 321.37 | 2.95 | 3.64 | 28.5 | 371.98 | 209.78 | 2442.7926 | 387.44 | 363.89 | 4237.3333 | 2.61 | 565.7 | 5.99 | 163.09 | 86.696
1082.21 | 567.7017 | 16.7223 | 565.5661 | 111.1711 | 18.8289 | 263.2376 | 1079.9121 | 130.3138 | 3.4394 | 563.5926 | 16.5473 | 565.5661 | 2.4688 | 13.4157 | 2.7424 | 18.452 | -92.4884 | 38.5116 | 2.72 | 321.18 | 3.48 | 3.68 | 29 | 366.78 | 205.64 | 2497.8937 | 370.9 | 348.84 | 4237.3333 | 2.5 | 565.97 | 5.83 | 161.72 | 84.648
947.404 | 567.8582 | 15.3442 | 565.1678 | 99.5627 | 5.6752 | 256.2338 | 947.9355 | 123.8287 | 3.4674 | 563.7269 | 15.1997 | 565.1678 | 2.1644 | 11.7742 | 2.4092 | 16.8547 | -93.0084 | 37.4802 | 2.4 | 321.87 | 3.64 | 3.79 | 26.5 | 359.2 | 177.21 | 2453.4334 | 326.1 | 306.06 | 4237.3333 | 2.2 | 565.89 | 5.28 | 155.01 | 86.779
899.5559 | 567.2818 | 13.8459 | 565.0909 | 91.4646 | 2.6714 | 253.4664 | 901.1612 | 121.7423 | 3.4647 | 563.0646 | 13.6966 | 565.0909 | 2.0554 | 11.2734 | 2.2907 | 15.3939 | -93.0533 | 37.4614 | 2.29 | 324.32 | 3.58 | 3.85 | 25.5 | 359.01 | 163.79 | 2394.7856 | 309.61 | 289.81 | 4237.3333 | 2.08 | 565.2 | 4.82 | 150.99 | 89.5837
907.3922 | 567.775 | 12.935 | 565.2949 | 99.7119 | 4.1371 | 254.0507 | 904.0152 | 124.0537 | 3.5654 | 563.5309 | 12.7674 | 565.2949 | 2.0734 | 11.3814 | 2.3112 | 14.5973 | -92.9475 | 37.7136 | 2.31 | 328.29 | 3.52 | 3.78 | 26.5 | 362.22 | 171.71 | 2484.0139 | 312.84 | 292.91 | 4237.3333 | 2.1 | 565.92 | 4.54 | 152.21 | 86.452
914.4844 | 567.7213 | 13.5619 | 566.0217 | 100.9275 | 4.1773 | 254.4104 | 912.9288 | 125.1497 | 3.3714 | 563.5112 | 13.4053 | 566.0217 | 2.0897 | 11.4554 | 2.3275 | 15.1667 | -92.8416 | 37.9658 | 2.33 | 326.39 | 3.17 | 3.37 | 27 | 362.02 | 173.32 | 2485.6651 | 315.95 | 295.46 | 4237.3333 | 2.13 | 566.02 | 4.75 | 151.9 | 86.1148
922.5469 | 566.9473 | 13.6504 | 564.3937 | 96.1712 | 6.1004 | 254.8612 | 919.0507 | 124.4825 | 3.5345 | 562.721 | 13.4906 | 564.3937 | 2.1082 | 11.5228 | 2.3476 | 15.2767 | -92.8615 | 37.8705 | 2.35 | 325.4 | 3.59 | 3.58 | 27 | 359.89 | 172.32 | 2452.8109 | 318.07 | 297.69 | 4237.3333 | 2.14 | 565.21 | 4.78 | 152.73 | 87.4744
951.7933 | 566.9096 | 14.0394 | 564.741 | 85.262 | 7.0394 | 256.2205 | 945.9513 | 124.8556 | 3.4713 | 562.6413 | 13.8729 | 564.741 | 2.1733 | 11.9149 | 2.4192 | 15.7543 | -93.0496 | 37.3285 | 2.41 | 325.13 | 3.6 | 3.73 | 28 | 361.01 | 177.61 | 2451.3624 | 327.71 | 307.01 | 4237.3333 | 2.2 | 565.04 | 4.93 | 152.25 | 87.2961
977.4501 | 567.0294 | 14.6689 | 565.3495 | 89.8176 | 10.1233 | 257.7959 | 974.0232 | 124.5784 | 3.4652 | 563.3152 | 14.5048 | 565.3495 | 2.2325 | 12.1612 | 2.4837 | 16.3715 | -92.7838 | 37.9335 | 2.47 | 324.7 | 3.66 | 4.03 | 27.5 | 364.17 | 186.87 | 2510.878 | 335.91 | 315.36 | 4237.3333 | 2.26 | 565.66 | 5.11 | 154.21 | 84.953
932.7111 | 567.5683 | 14.2167 | 564.7867 | 91.117 | 5.6756 | 255.4952 | 931.9992 | 124.9429 | 3.6009 | 563.3367 | 14.0613 | 564.7867 | 2.1306 | 11.6621 | 2.3724 | 15.872 | -92.7741 | 38.0194 | 2.38 | 324.58 | 3.26 | 3.71 | 28 | 363.05 | 180.7 | 2535.8884 | 322.29 | 301.94 | 4237.3333 | 2.17 | 565.52 | 4.98 | 154.07 | 83.9761
914.441 | 567.869 | 14.4978 | 565.592 | 96.5421 | 3.58 | 254.7471 | 916.9492 | 124.7822 | 3.3862 | 563.6553 | 14.3596 | 565.592 | 2.0898 | 11.422 | 2.3285 | 16.0438 | -92.8433 | 37.6269 | 2.32 | 323.1 | 3.54 | 3.74 | 28 | 358.23 | 171.9 | 2476.8689 | 314.04 | 294.08 | 4237.3333 | 2.12 | 565.94 | 4.99 | 153.25 | 86.5006
926.5022 | 566.9095 | 14.6102 | 565.1106 | 81.0345 | 4.4267 | 254.7377 | 928.2303 | 123.6298 | 3.5382 | 563.0646 | 14.4673 | 565.1106 | 2.1166 | 11.5674 | 2.3578 | 16.2034 | -92.7296 | 37.9955 | 2.35 | 323.22 | 3.36 | 3.75 | 27 | 360.56 | 173.94 | 2477.7844 | 317.79 | 297.46 | 4237.3333 | 2.14 | 565.31 | 5.04 | 152.37 | 86.6874
944.6483 | 566.8513 | 14.8274 | 564.6757 | 84.6498 | 7.3893 | 255.5652 | 948.6485 | 125.7466 | 3.5447 | 563.2767 | 14.6816 | 564.6757 | 2.1581 | 11.7935 | 2.4031 | 16.4653 | -92.755 | 37.8546 | 2.41 | 323.07 | 3.47 | 3.89 | 27.5 | 363.7 | 180.45 | 2500.4964 | 326.84 | 305.79 | 4237.3333 | 2.2 | 565.1 | 5.17 | 152.18 | 85.0664
970.1997 | 567.6945 | 15.2264 | 565.4158 | 97.8119 | 10.6189 | 256.7805 | 970.8537 | 125.2377 | 3.3815 | 563.854 | 15.079 | 565.4158 | 2.2156 | 12.0638 | 2.4646 | 16.8485 | -92.6518 | 37.9832 | 2.46 | 322.64 | 3.18 | 3.65 | 27.5 | 363.27 | 182.88 | 2484.6052 | 332.82 | 311.89 | 4237.3333 | 2.24 | 565.95 | 5.27 | 156.43 | 86.2295
972.4657 | 566.6876 | 15.3466 | 565.1849 | 97.4683 | 12.4581 | 256.9733 | 970.1078 | 126.8281 | 3.4668 | 562.6727 | 15.1975 | 565.1849 | 2.2212 | 12.0586 | 2.4713 | 16.959 | -92.72 | 37.9652 | 2.48 | 321.97 | 3.37 | 3.59 | 27.5 | 361.69 | 182.24 | 2453.2567 | 335.9 | 314.77 | 4237.3333 | 2.27 | 565.6 | 5.33 | 156.54 | 86.8092
943.5665 | 567.1316 | 14.9 | 564.7223 | 90.0736 | 7.4999 | 255.4298 | 947.4301 | 125.0086 | 3.3351 | 563.2839 | 14.756 | 564.7223 | 2.1544 | 11.7724 | 2.3988 | 16.4973 | -92.9834 | 37.3098 | 2.4 | 322.45 | 3.44 | 3.58 | 27 | 360.06 | 176.61 | 2454.7512 | 325.81 | 304.86 | 4237.3333 | 2.2 | 564.95 | 5.17 | 154.7 | 86.8302
929.9461 | 568.3335 | 15.0188 | 566.291 | 79.0482 | 3.8582 | 255.0651 | 929.7481 | 122.0707 | 3.4309 | 564.2495 | 14.8845 | 566.291 | 2.1242 | 11.6021 | 2.3659 | 16.5781 | -92.8986 | 37.5633 | 2.37 | 322.19 | 3.4 | 3.93 | 26.5 | 360.94 | 178.62 | 2524.002 | 320.98 | 299.87 | 4237.3333 | 2.16 | 565.6 | 5.2 | 154.16 | 84.7185
924.2952 | 567.2703 | 14.9663 | 565.9223 | 102.4951 | 10.988 | 254.9364 | 936.5223 | 128.6394 | 3.4298 | 563.4942 | 14.828 | 565.9223 | 2.1127 | 11.6567 | 2.3522 | 16.4823 | -93.0667 | 37.1507 | 2.34 | 321.46 | 3.63 | 3.84 | 27.5 | 361.88 | 185.92 | 2648.0841 | 318.98 | 297.5 | 4237.3333 | 2.14 | 566.61 | 5.11 | 153.93 | 80.8016
948.8857 | 567.4465 | 15.0761 | 565.2967 | 93.8736 | 6.9977 | 255.852 | 949.9961 | 131.055 | 3.4484 | 563.3608 | 14.9332 | 565.2967 | 2.1682 | 11.8328 | 2.4127 | 16.6532 | -93.0657 | 37.1225 | 2.4 | 322.52 | 3.31 | 3.57 | 27.5 | 363.92 | 184.75 | 2562.344 | 326.68 | 305.52 | 4237.3333 | 2.2 | 566.18 | 5.19 | 154.7 | 83.5043
1006.2315 | 567.1351 | 15.9492 | 566.0458 | 73.0426 | 7.1461 | 259.3608 | 1032.8682 | 128.4011 | 3.2937 | 563.0986 | 15.7876 | 566.0458 | 2.2972 | 12.8144 | 2.5544 | 17.7675 | -92.819 | 37.6652 | 2.53 | 318.56 | 3.02 | 3.56 | 28 | 365.87 | 187.21 | 2433.4965 | 347.48 | 325.98 | 4237.3333 | 2.31 | 565.61 | 5.57 | 156.57 | 85.9072
1068.7229 | 567.0151 | 16.6568 | 566.2203 | 84.7352 | 11.2912 | 263.2277 | 1086.7195 | 126.3624 | 3.5093 | 563.1613 | 16.482 | 566.2203 | 2.438 | 13.5136 | 2.7083 | 18.5581 | -92.4463 | 38.4674 | 2.7 | 319.14 | 2.93 | 3.65 | 27.5 | 369.84 | 192.88 | 2340.2155 | 371.02 | 349.24 | 4237.3333 | 2.48 | 566.25 | 5.88 | 161.13 | 88.4069
963.3834 | 567.1888 | 15.5635 | 564.4904 | 89.3821 | 3.9873 | 257.4735 | 970.1694 | 124.0094 | 3.2924 | 563.2257 | 15.4207 | 564.4904 | 2.1998 | 12.06 | 2.4483 | 17.2067 | -92.7398 | 37.8892 | 2.43 | 320.61 | 2.67 | 3.52 | 27 | 361.97 | 172.99 | 2362.5872 | 329.71 | 310.26 | 4237.3333 | 2.22 | 565.6 | 5.37 | 155.64 | 89.8551
890.9416 | 567.6649 | 14.387 | 565.5437 | 83.4888 | 1.647 | 253.525 | 895.8832 | 123.2685 | 3.4988 | 563.8262 | 14.2579 | 565.5437 | 2.0369 | 11.1603 | 2.27 | 15.8985 | -92.8181 | 37.822 | 2.28 | 322.63 | 3.57 | 3.99 | 27.5 | 360.27 | 164.77 | 2421.9843 | 307.55 | 288.27 | 4237.3333 | 2.08 | 565.79 | 4.96 | 150.91 | 88.0527
882.8079 | 567.5906 | 14.1581 | 566.0118 | 102.1479 | 3.1749 | 252.9155 | 886.7798 | 124.6402 | 3.4686 | 563.6606 | 14.0285 | 566.0118 | 2.0194 | 11.0502 | 2.2505 | 15.58 | -93.0383 | 37.2157 | 2.25 | 323.38 | 4.07 | 4.06 | 27.5 | 357.56 | 169.38 | 2522.74 | 303.77 | 284.5 | 4237.3333 | 2.05 | 565.84 | 4.84 | 149.64 | 85.0189
917.6121 | 567.5208 | 14.6219 | 566.0726 | 106.958 | 6.5227 | 254.7752 | 915.165 | 127.1873 | 3.3209 | 563.5971 | 14.4907 | 566.0726 | 2.0977 | 11.435 | 2.3352 | 16.0859 | -92.7503 | 37.9052 | 2.33 | 323.13 | 3.52 | 3.58 | 28 | 357.98 | 179.69 | 2584.5432 | 314.09 | 294.6 | 4237.3333 | 2.12 | 566.3 | 5 | 153.37 | 83.296
945.4759 | 567.8726 | 15.211 | 565.8122 | 100.8505 | 4.1455 | 256.4681 | 947.3111 | 125.7781 | 3.4814 | 563.9032 | 15.0765 | 565.8122 | 2.161 | 11.8012 | 2.4054 | 16.7672 | -92.6009 | 38.2405 | 2.4 | 321.62 | 3.26 | 3.67 | 27.5 | 359.91 | 179.24 | 2498.1075 | 323.72 | 304.03 | 4237.3333 | 2.19 | 565.82 | 5.24 | 154.96 | 85.5512